## INDEX (2)
PAGE | REVISION | [6 empty] | PAGE | REVISION | [6 empty] | PAGE | REVISION
| 0 | 1 | 2 | 3 | 4 | 5 | 6 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | x | [6 empty] | 79 | [7 empty] | 157
2 | x | [6 empty] | 80 | [7 empty] | 158
3 | x | [6 empty] | 81 | [7 empty] | 159
4 | x | [6 empty] | 82 | [7 empty] | 160
5 | x | [6 empty] | 83 | [7 empty] | 161
6 | x | [6 empty] | 84 | [7 empty] | 162
7 | x | [6 empty] | 85 | [7 empty] | 163
8 | x | [6 empty] | 86 | [7 empty] | 164
9 | [7 empty] | 87 | [7 empty] | 165
10 | [7 empty] | 88 | [7 empty] | 166
11 | [7 empty] | 89 | [7 empty] | 167
12 | [7 empty] | 90 | [7 empty] | 168
13 | [7 empty] | 91 | [7 empty] | 169
14 | [7 empty] | 92 | [7 empty] | 170
15 | [7 empty] | 93 | [7 empty] | 171
16 | [7 empty] | 94 | [7 empty] | 172
17 | [7 empty] | 95 | [7 empty] | 173
18 | [7 empty] | 96 | [7 empty] | 174
19 | [7 empty] | 97 | [7 empty] | 175
20 | [7 empty] | 98 | [7 empty] | 176
21 | [7 empty] | 99 | [7 empty] | 177
22 | [7 empty] | 100 | [7 empty] | 178
23 | [7 empty] | 101 | [7 empty] | 179
24 | [7 empty] | 102 | [7 empty] | 180
25 | [7 empty] | 103 | [7 empty] | 181
26 | [7 empty] | 104 | [7 empty] | 182
27 | [7 empty] | 105 | [7 empty] | 183
28 | [7 empty] | 106 | [7 empty] | 184
29 | [7 empty] | 107 | [7 empty] | 185
30 | [7 empty] | 108 | [7 empty] | 186
31 | [7 empty] | 109 | [7 empty] | 187
32 | [7 empty] | 110 | [7 empty] | 188
33 | [7 empty] | 111 | [7 empty] | 189
34 | [7 empty] | 112 | [7 empty] | 190
35 | [7 empty] | 113 | [7 empty] | 191
36 | [7 empty] | 114 | [7 empty] | 192
37 | [7 empty] | 115 | [7 empty] | 193
38 | [7 empty] | 116 | [7 empty] | 194
39 | [7 empty] | 117 | [7 empty] | 195
40 | [7 empty] | 118 | [7 empty] | 196
41 | [7 empty] | 119 | [7 empty] | 197
42 | [7 empty] | 120 | [7 empty] | 198
43 | [7 empty] | 121 | [7 empty] | 199
44 | [7 empty] | 122 | [7 empty] | 200
45 | [7 empty] | 123 | [7 empty] | 201
46 | [7 empty] | 124 | [7 empty] | 202
47 | [7 empty] | 125 | [7 empty] | 203
48 | [7 empty] | 126 | [7 empty] | 204
49 | [7 empty] | 127 | [7 empty] | 205
50 | [7 empty] | 128 | [7 empty] | 206
51 | [7 empty] | 129 | [7 empty] | 207
52 | [7 empty] | 130 | [7 empty] | 208
53 | [7 empty] | 131 | [7 empty] | 209
54 | [7 empty] | 132 | [7 empty] | 210
55 | [7 empty] | 133 | [7 empty] | 211
56 | [7 empty] | 134 | [7 empty] | 212
57 | [7 empty] | 135 | [7 empty] | 213
58 | [7 empty] | 136 | [7 empty] | 214
59 | [7 empty] | 137 | [7 empty] | 215
60 | [7 empty] | 138 | [7 empty] | 216
61 | [7 empty] | 139 | [7 empty] | 217
62 | [7 empty] | 140 | [7 empty] | 218
63 | [7 empty] | 141 | [7 empty] | 219
64 | [7 empty] | 142 | [7 empty] | 220
65 | [7 empty] | 143 | [7 empty] | 221
66 | [7 empty] | 144 | [7 empty] | 222
67 | [7 empty] | 145 | [7 empty] | 223
68 | [7 empty] | 146 | [7 empty] | 224
69 | [7 empty] | 147 | [7 empty] | 225
70 | [7 empty] | 148 | [7 empty] | 226
71 | [7 empty] | 149 | [7 empty] | 227
72 | [7 empty] | 150 | [7 empty] | Appendix
73 | [7 empty] | 151
74 | [7 empty] | 152 | [7 empty] | Att. 1
75 | [7 empty] | 153 | [7 empty] | Att. 2
76 | [7 empty] | 154 | [7 empty] | Att. 3
77 | [7 empty] | 155 | [7 empty] | Att. 4
78 | [7 empty] | 156 | [7 empty] | Att. 5

## Abbreviation
Abbreviation
DI= Digital Input DO= Digital Output AI=Analogue Input AO=Analogue Output DIR= Digital Input Redundant DOR= Digital Output Redundant AIR=Analogue Input Redundant AOR=Analogue Output Redundant PB= Push Button Note:
40-SOV-823A3
40-SOV-823A4
40-SOV-827A
40-SOV-829A
40-SOV-828A
DIR
|  | DIR | 40-RFU-821A
| 40-ESD-821A | DIR
40-XL-RFU821A
40-TS-RFU821A"

## HW IO LIST
Toase-ehe Park Sanati Gohar Ofogh Petrochemical Co. CONCEPTUAL, BASIC and DETAIL DESIGN ENGINEERING OF STYRENE PARK OFFSITE
Document Title: IO List
|  | Document No.: EI027-HSE-VD – IN– LST– 005-R1 | [8 empty] | Rev. R1 | Page 2 of 3
No. | Signal Name : ANALOGUE INPUT |  | Tag. No. |  | Content of signal | SIGNAL Type | Scale Range | Unit | From | To | IS/NIS | Remarks
1 | Compressor Suction pressure transmitter |  | PIT-RU0001A-01 | 300-PISA-4100A | 4 to 20mA / 2-wire | AI | -1.0 to 10.3 | barG | Field | RU0001 | IS
2 | Discharge pressure transmitter |  | PIT-RU0001A-03 | 300-PISA-4100A | 4 to 20mA / 2-wire | AI | -1.0 to 27.6 | barG | Field | RU0001 | IS
3 | Oil header Compressor pressure transmitter |  | PIT-RU0001A-02 | 300-PISA-4100A | 4 to 20mA / 2-wire | AI | -1.0 to 27.6 | barG | Field | RU0001 | IS
4 | Upstream oil filter pressure transmitter |  | PIT-RU0001A-05 | 300-PISA-4100A | 4 to 20mA / 2-wire | AI | -1.0 to 27.6 | barG | Field | RU0001 | IS
5 | Downstream oil filter pressure transmitter |  | PIT-RU0001A-06 | 300-PISA-4100A | 4 to 20mA / 2-wire | AI | -1.0 to 27.6 | barG | Field | RU0001 | IS
6 | Pressure transmitter oil separator |  | PIT-RU0001A-04 | 300-PISA-4100A | 4 to 20mA / 2-wire | AI | -1.0 to 27.6 | barG | Field | RU0001 | IS
7 | Compressor Suction temperature transmitter |  | TIT-RU0001A-01 | 300-PISA-4100A | 4 to 20mA / 2-wire | AI | -50.0 to 100 | °C | Field | RU0001 | IS
8 | Oil Separator temperature transmitter |  | TIT-RU0001A-03 | 300-PISA-4100A | 4 to 20mA / 2-wire | AI | -50.0 to 100 | °C | Field | RU0001 | IS
9 | Oil header compressor temperature transmitter |  | TIT-RU0001A-02 | 300-PISA-4100A | 4 to 20mA / 2-wire | AI | -50.0 to 100 | °C | Field | RU0001 | IS
10 | Compressor slide valve position transmitter |  | ZIT-RU0001A-01 | 300-PISA-4100A | 4 to 20mA / 2-wire | AI | 0.0 to 100.0 | % | Field | RU0001 | IS
11 | Compressor Suction pressure transmitter |  | PIT-RU0001B-01 | 300-PISA-4100A | 4 to 20mA / 2-wire | AI | -1.0 to 10.3 | barG | Field | RU0001 | IS | (Unit B)
12 | Discharge pressure transmitter |  | PIT-RU0001B-03 | 300-PISA-4100A | 4 to 20mA / 2-wire | AI | -1.0 to 27.6 | barG | Field | RU0001 | IS | (Unit B)
13 | Oil header Compressor pressure transmitter |  | PIT-RU0001B-02 | 300-PISA-4100A | 4 to 20mA / 2-wire | AI | -1.0 to 27.6 | barG | Field | RU0001 | IS | (Unit B)
14 | Upstream oil filter pressure transmitter |  | PIT-RU0001B-05 | 300-PISA-4100A | 4 to 20mA / 2-wire | AI | -1.0 to 27.6 | barG | Field | RU0001 | IS | (Unit B)
15 | Downstream oil filter pressure transmitter |  | PIT-RU0001B-06 | 300-PISA-4100A | 4 to 20mA / 2-wire | AI | -1.0 to 27.6 | barG | Field | RU0001 | IS | (Unit B)
16 | Pressure transmitter oil separator |  | PIT-RU0001B-04 | 300-PISA-4100A | 4 to 20mA / 2-wire | AI | -1.0 to 27.6 | barG | Field | RU0001 | IS | (Unit B)
17 | Compressor Suction temperature transmitter |  | TIT-RU0001B-01 | 300-PISA-4100A | 4 to 20mA / 2-wire | AI | -50.0 to 100 | °C | Field | RU0001 | IS | (Unit B)
18 | Oil Separator temperature transmitter |  | TIT-RU0001B-03 | 300-PISA-4100A | 4 to 20mA / 2-wire | AI | -50.0 to 100 | °C | Field | RU0001 | IS | (Unit B)
19 | Oil header compressor temperature transmitter |  | TIT-RU0001B-02 | 300-PISA-4100A | 4 to 20mA / 2-wire | AI | -50.0 to 100 | °C | Field | RU0001 | IS | (Unit B)
20 | Compressor slide valve position transmitter |  | ZIT-RU0001B-01 | 300-PISA-4100A | 4 to 20mA / 2-wire | AI | 0.0 to 100.0 | % | Field | RU0001 | IS | (Unit B)
21 | Chiller level transmitter |  | LIT-RU0001A-01 | 300-PISA-4100A | 4 to 20mA / 2-wire | AI | 0.0 to 100.0 | % | Field | RU0001 | IS
22 | Chiller level transmitter |  | LIT-RU0001B-01 | 300-PISA-4100A | 4 to 20mA / 2-wire | AI | 0.0 to 100.0 | % | Field | RU0001 | IS | (Unit B)
23 | Compressor motor amperage |  | II-RU0001A-01 | 300-PISA-4100A | 4 to 20mA / 2-wire | AI | 0 to 200 | Amp | MCC | RU0001 | NIS | Amperage convertor towards 4-20mA located in MCC
24 | Compressor motor amperage |  | II-RU0001B-01 | 300-PISA-4100A | 4 to 20mA / 2-wire | AI | 0 to 200 | Amp | MCC | RU0001 | NIS | Amperage convertor towards 4-20mA located in MCC (outside vendor scope of supply)
25 | Compressor A motor winding U temperature |  | PTC-RU0001A-13 | 300-PISA-4100A | PTC |  | 0 to 150 | °C | Field | MCC
26 | Compressor A motor winding V temperature |  | PTC-RU0001A-14 | 300-PISA-4100A | PTC |  | 0 to 150 | °C | Field | MCC
27 | Compressor A motor winding W temperature |  | PTC-RU0001A-15 | 300-PISA-4100A | PTC |  | 0 to 150 | °C | Field | MCC
28 | Compressor B motor winding U temperature |  | PTC-RU0001B-13 | 300-PISA-4100A | PTC |  | 0 to 150 | °C | Field | MCC |  | (Unit B)
29 | Compressor B motor winding V temperature |  | PTC-RU0001B-14 | 300-PISA-4100A | PTC |  | 0 to 150 | °C | Field | MCC |  | (Unit B)
30 | Compressor B motor winding W temperature |  | PTC-RU0001B-15 | 300-PISA-4100A | PTC |  | 0 to 150 | °C | Field | MCC |  | (Unit B)
31 | Chiller level control valve |  | LV-RU0001A-01 | 300-PISA-4100A | 4 to 20mA / 2-wire | AO | 0.0 to 100.0 | % | RU0001 | Field | IS
32 | Chiller level control valve |  | LV-RU0001B-01 | 300-PISA-4100A | 4 to 20mA / 2-wire | AO | 0.0 to 100.0 | % | RU0001 | Field | IS | (Unit B)
33 | Condensor VFD control |  | PIC-RU0001A-04 | 300-PISA-4100A | 4 to 20mA / 2-wire | AO | 0.0 to 100.0 | % | RU0001 | MCC (VFD) | NIS
34 | Condensor VFD control |  | PIC-RU0001A-04 | 300-PISA-4100A | 4 to 20mA / 2-wire | AO | 0.0 to 100.0 | % | RU0001 | MCC (VFD) | NIS | (Unit B)
35 | Compressor capacity load Return solenoid valve |  | SOV-RU0001A-01D |  | 24Vdc / **W | DO | 1 = Energized | Status | RU0001 | Field | NIS
36 | Compressor capacity unload supply solenoid valve |  | SOV-RU0001A-01A |  | 24Vdc / **W | DO | 1 = Energized | Status | RU0001 | Field | NIS
37 | Compressor capacity load supply solenoid valve |  | SOV-RU0001A-01C |  | 24Vdc / **W | DO | 1 = Energized | Status | RU0001 | Field | NIS
38 | Compressor capacity unload Return solenoid valve |  | SOV-RU0001A-01E |  | 24Vdc / **W | DO | 1 = Energized | Status | RU0001 | Field | NIS
39 | Compressor capacity load Return solenoid valve |  | SOV-RU0001B-01D |  | 24Vdc / **W | DO | 1 = Energized | Status | RU0001 | Field | NIS | (Unit B)
40 | Compressor capacity unload supply solenoid valve |  | SOV-RU0001B-01A |  | 24Vdc / **W | DO | 1 = Energized | Status | RU0001 | Field | NIS | (Unit B)
41 | Compressor capacity load supply solenoid valve |  | SOV-RU0001B-01C |  | 24Vdc / **W | DO | 1 = Energized | Status | RU0001 | Field | NIS | (Unit B)
42 | Compressor capacity unload Return solenoid valve |  | SOV-RU0001B-01E |  | 24Vdc / **W | DO | 1 = Energized | Status | RU0001 | Field | NIS | (Unit B)
43 | Hot gas solenoid valve |  | SOV-RU0001A-03 | 300-XY-4006A | 24Vdc / **W | DO | 1 = Energized | Status | RU0001 | Field | NIS
44 | Evaporator oil drain line. |  | SOV-RU0001A-02 | 300-XY-4006A | 24Vdc / **W | DO | 1 = Energized | Status | RU0001 | Field | NIS
45 | Hot gas solenoid valve |  | SOV-RU0001B-03 | 300-XY-4006A | 24Vdc / **W | DO | 1 = Energized | Status | RU0001 | Field | NIS | (Unit B)
46 | Evaporator oil drain line. |  | SOV-RU0001B-02 | 300-XY-4006A | 24Vdc / **W | DO | 1 = Energized | Status | RU0001 | Field | NIS | (Unit B)
47 | Oil heater temp. control switch |  | TS-RU0001A-01A | 300-TS-4230C | 24Vdc / **D | DI | 1 = Low Temp. | Status | Field | RU0001 | NIS
48 | Oil heater Surface and box temp. control switch |  | TS-RU0001A-01B | 300-TS-4230C | 24Vdc / **D | DI | 1 = Low Temp. | Status | Field | RU0001 | NIS
49 | Oil heater temp. control switch |  | TS-RU0001B-01A | 300-TS-4230C | 24Vdc / **D | DI | 1 = Low Temp. | Status | Field | RU0001 | NIS | (Unit B)
50 | Oil heater Surface and box temp. control switch |  | TS-RU0001B-01B | 300-TS-4230C | 24Vdc / **D | DI | 1 = Low Temp. | Status | Field | RU0001 | NIS | (Unit B)
51 | Oil separator level switch |  | LS-RU0001A-01 | 300-TS-4230C | 24Vdc / **D | DI | 1 = Low Level | Status | Field | RU0001 | NIS
52 | Oil separator level switch |  | LS-RU0001B-01 | 300-TS-4230C | 24Vdc / **D | DI | 1 = Low Level | Status | Field | RU0001 | NIS | (Unit B)
53 | Compressor A running lamp |  | XL-RU0001A-06 | 300-XL-4150A | 24Vdc / <=1W | DO | 1 = Running | Status | RU0001 | RU0001A-LCP-01 | NIS
54 | Compressor B running lamp |  | XL-RU0001B-06 | 300-XL-4150A | 24Vdc / <=1W | DO | 1 = Running | Status | RU0001 | RU0001B-LCP-01 | NIS | (Unit B)
55 | Oil pump running lamp |  | HLR-RU0001A-06 | 300-XL-4300A | 24Vdc / <=1W | DO | 1 = Running | Status | RU0001 | RU0001A-LCP-01 | NIS
56 | Oil pump running lamp |  | HLR-RU0001B-06 | 300-XL-4300A | 24Vdc / <=1W | DO | 1 = Running | Status | RU0001 | RU0001B-LCP-01 | NIS | (Unit B)
57 | Unit A start PB |  | HST-RU0001A-01 | 300-HS-4101A | Dry contact | DI | 1 = Start | Pulse | RU0001A-LCP-01 | RU0001 | NIS
58 | Unit A stop PB |  | HSP--RU0001A-01 | 300-HS-4101A | Dry contact | DI | 0 = Stop | Pulse | RU0001A-LCP-01 | RU0001 | NIS
59 | Unit B start PB |  | HST-RU0001B-01 | 300-HS-4101A | Dry contact | DI | 1 = Start | Pulse | RU0001B-LCP-01 | RU0001 | NIS | (Unit B)
60 | Unit B stop PB |  | HSP--RU0001B-01 | 300-HS-4101A | Dry contact | DI | 0 = Stop | Pulse | RU0001B-LCP-01 | RU0001 | NIS | (Unit B)
61 | Oil pump auto select SW |  | HSC--RU0001A-06A | 300-HS-4101A | Dry contact | DI | 1 = Auto | Pulse | RU0001A-LCP-01 | RU0001 | NIS
62 | Oil pump Manual select SW |  | HSC--RU0001A-06B | 300-HS-4101A | Dry contact | DI | 1 = Manual | Pulse | RU0001A-LCP-01 | RU0001 | NIS
63 | Oil pump start PB |  | HST-RU0001A-06 | 300-HS-4101A | Dry contact | DI | 1 = Start | Pulse | RU0001A-LCP-01 | RU0001 | NIS
64 | Oil pump stop PB |  | HSP--RU0001A-06 | 300-HS-4101A | Dry contact | DI | 0 = Stop | Pulse | RU0001A-LCP-01 | RU0001 | NIS
65 | Oil pump auto select SW |  | HSC--RU0001B-06A | 300-HS-4101A | Dry contact | DI | 1 = Auto | Pulse | RU0001B-LCP-01 | RU0001 | NIS | (Unit B)
66 | Oil pump Manual select SW |  | HSC--RU0001B-06B | 300-HS-4101A | Dry contact | DI | 1 = Manual | Pulse | RU0001B-LCP-01 | RU0001 | NIS | (Unit B)
67 | Oil pump start PB |  | HST-RU0001B-06 | 300-HS-4101A | Dry contact | DI | 1 = Start | Pulse | RU0001B-LCP-01 | RU0001 | NIS | (Unit B)
68 | Oil pump stop PB |  | HSP--RU0001B-06 | 300-HS-4101A | Dry contact | DI | 0 = Stop | Pulse | RU0001B-LCP-01 | RU0001 | NIS | (Unit B)
69 | UNIT A Remote / local select SW-Local |  | HSC--RU0001A-01 | 300-HS-4101A | Dry contact | DI | 1 =Local | Pulse | RU0001A-LCP-01 | RU0001 | NIS
70 | UNIT B Remote / local select SW-Local |  | HSC--RU0001B-01 | 300-HS-4101A | Dry contact | DI | 1 =Local | Pulse | RU0001B-LCP-01 | RU0001 | NIS | (Unit B)
71 | Compressor A capacity control load select SW |  | HS--RU0001A-02A | 300-HS-4101A | Dry contact | DI | 1 = Load | Pulse | RU0001A-LCP-01 | RU0001 | NIS
72 | Compressor A capacity control unload select SW |  | HS--RU0001A-02B | 300-HS-4101A | Dry contact | DI | 1 = Unload | Pulse | RU0001A-LCP-01 | RU0001 | NIS
73 | Compressor A capacity Control Local/Auto select. SW |  | HS--RU0001A-01 | 300-HS-4101A | Dry contact | DI | 1 =Local | Pulse | RU0001A-LCP-01 | RU0001 | NIS
74 | Compressor B capacity control load select SW |  | HS--RU0001B-02A | 300-HS-4101A | Dry contact | DI | 1 = Load | Pulse | RU0001B-LCP-01 | RU0001 | NIS | (Unit B)
75 | Compressor B capacity control unload select SW |  | HS--RU0001B-02B | 300-HS-4101A | Dry contact | DI | 1 = Unload | Pulse | RU0001B-LCP-01 | RU0001 | NIS | (Unit B)
76 | Compressor B capacity Control Local/Auto select. SW |  | HS--RU0001B-01 | 300-HS-4101A | Dry contact | DI | 1 =Local | Pulse | RU0001B-LCP-01 | RU0001 | NIS | (Unit B)
77 | Lamp test PB |  | HS-RU0001A-03 | 300-HS-4104A | Dry contact | DI | 1 = Test | Pulse | RU0001A-LCP-01 | RU0001 | NIS
78 | Local panel Emergency stop PB |  | HSS-RU0001A-01 | 300-HS-4104A | Dry contact | DI | 0 = Emergency stop | Pulse | RU0001A-LCP-01 | RU0001 | NIS
79 | Unit A ready to start lamp |  | XL-RU0001A-05 | 300-XL-4103A | 24Vdc / <=1W | DO | 1 = Ready | Status | RU0001 | RU0001A-LCP-01 | NIS
80 | Unit A Common alarm lamp |  | XA-RU0001A-01 | 300-XL-4101A | 24Vdc / <=1W | DO | 1 = Alarm | Status | RU0001 | RU0001A-LCP-01 | NIS
81 | Unit A Common trip lamp |  | XA-RU0001A-02 | 300-XL-4101A | 24Vdc / <=1W | DO | 1 = Trip | Status | RU0001 | RU0001A-LCP-01 | NIS
82 | Unit B ready to start lamp |  | XL-RU0001B-05 | 300-XL-4103A | 24Vdc / <=1W | DO | 1 = Ready | Status | RU0001 | RU0001B-LCP-01 | NIS | (Unit B)
83 | Unit B Common alarm lamp |  | XA-RU0001B-01 | 300-XL-4101A | 24Vdc / <=1W | DO | 1 = Alarm | Status | RU0001 | RU0001B-LCP-01 | NIS | (Unit B)
84 | Unit B Common trip lamp |  | XA-RU0001B-02 | 300-XL-4101A | 24Vdc / <=1W | DO | 1 = Trip | Status | RU0001 | RU0001B-LCP-01 | NIS | (Unit B)
85 | Lamp test PB |  | HS-RU0001B-03 | 300-HS-4104A | Dry contact | DI | 1 = Test | Pulse | RU0001A-LCP-01 | RU0001 | NIS
86 | Local panel Emergency stop PB |  | HSS-RU0001B-01 | 300-HS-4104A | Dry contact | DI | 0 = Emergency stop | Pulse | RU0001A-LCP-01 | RU0001 | NIS
87 | Compressor RU0001A-M-01 motor start command |  | XST-RU0001A-01 | 300-XS-4100A | Dry contact | DO | 1 = Start | Pulse | RU0001 | MCC
88 | Compressor RU0001A-M-01 motor stop command |  | XSP-RU0001A-01 | 300-XS-4100A | Dry contact | DO | 0= Stop | Pulse | RU0001 | MCC
89 | Compressor RU0001A-M-01 motor running status |  | XL-RU0001A-01 | 300-XS-4100A | Dry contact | DI | 1 = Running | Status | MCC | RU0001
90 | Compressor RU0001A-M-01 motor fault status |  | XF-RU0001A-01 | 300-XS-4100A | Dry contact | DI | 0= Fault | Status | MCC | RU0001
91 | Compressor RU0001B-M-01 motor start command |  | XST-RU0001B-01 | 300-XS-4100A | Dry contact | DO | 1 = Start | Pulse | RU0001 | MCC |  | (Unit B)
92 | Compressor RU0001B-M-01 motor stop command |  | XSP-RU0001B-01 | 300-XS-4100A | Dry contact | DO | 0= Stop | Pulse | RU0001 | MCC |  | (Unit B)
93 | Compressor RU0001B-M-01 motor running status |  | XL-RU0001B-01 | 300-XS-4100A | Dry contact | DI | 1 = Running | Status | MCC | RU0001 |  | (Unit B)
94 | Compressor RU0001B-M-01 motor fault status |  | XF-RU0001B-01 | 300-XS-4100A | Dry contact | DI | 0= Fault | Status | MCC | RU0001 |  | (Unit B)
95 | Oil pump RU0001A-P-01 motor start command |  | XST-RU0001A-02 | 300-XS-4100A | Dry contact | DO | 1 = Start | Pulse | RU0001 | MCC
96 | Oil pump RU0001A-P-01 motor stop command |  | XSP-RU0001A-02 | 300-XS-4100A | Dry contact | DO | 0= Stop | Pulse | RU0001 | MCC
97 | Oil pump RU0001A-P-01 motor running status |  | XL-RU0001A-03 | 300-XS-4100A | Dry contact | DI | 1 = Running | Status | MCC | RU0001
98 | Oil pump RU0001A-P-01 motor fault status |  | XF-RU0001A-03 | 300-XS-4100A | Dry contact | DI | 0= Fault | Status | MCC | RU0001
99 | Oil pump RU0001B-P-01 motor start command |  | XST-RU0001B-02 | 300-XS-4100A | Dry contact | DO | 1 = Start | Pulse | RU0001 | MCC |  | (Unit B)
100 | Oil pump RU0001B-P-01 motor stop command |  | XSP-RU0001B-02 | 300-XS-4100A | Dry contact | DO | 0= Stop | Pulse | RU0001 | MCC |  | (Unit B)
101 | Oil pump RU0001B-P-01 motor running status |  | XL-RU0001B-03 | 300-XS-4100A | Dry contact | DI | 1 = Running | Status | MCC | RU0001 |  | (Unit B)
102 | Oil pump RU0001B-P-01 motor fault status |  | XF-RU0001B-03 | 300-XS-4100A | Dry contact | DI | 0= Fault | Status | MCC | RU0001 |  | (Unit B)
103 | Separator oil heater RU0001A-H-01 On command |  | XS-RU0001A-01B | 300-XS-4100A | Dry contact | DO | 1 = On | Pulse | RU0001 | MCC
104 | Separator oil heater RU0001A-H-01 Off command |  | XS-RU0001A-01C | 300-XS-4100A | Dry contact | DO | 0= Off | Pulse | RU0001 | MCC
105 | Separator oil heater RU0001A-H-01 Running status |  | XL-RU0001A-02 | 300-XS-4100A | Dry contact | DI | 1 = On | Status | MCC | RU0001
106 | Separator oil heater RU0001A-H-01 fault status |  | XF-RU0001A-02 | 300-XS-4100A | Dry contact | DI | 0= Fault | Status | MCC | RU0001
107 | Separator oil heater RU0001B-H-01 On command |  | XS-RU0001B-01B | 300-XS-4100A | Dry contact | DO | 1 = On | Pulse | RU0001 | MCC |  | (Unit B)
108 | Separator oil heater RU0001B-H-01 Off command |  | XS-RU0001B-01C | 300-XS-4100A | Dry contact | DO | 0= Off | Pulse | RU0001 | MCC |  | (Unit B)
109 | Separator oil heater RU0001B-H-01 Running status |  | XL-RU0001B-02 | 300-XS-4100A | Dry contact | DI | 1 = On | Status | MCC | RU0001 |  | (Unit B)
110 | Separator oil heater RU0001B-H-01 fault status |  | XF-RU0001B-02 | 300-XS-4100A | Dry contact | DI | 0= Fault | Status | MCC | RU0001 |  | (Unit B)
111 | ESD trip signal to package A |  | ESD-RU0001A-02 | 300-XA-4002A | Dry contact | DI | 0 = Trip | Pulse | Plant ESD | RU0001
112 | UCP ESD trip signal |  | ESD-RU0001A-01 | 300-XA-4002A | Dry contact | DI | 0 = Trip | Pulse | RU0001 | RU0001
113 | ESD trip signal to package B |  | ESD-RU0001B-02 | 300-XA-4002A | Dry contact | DI | 0 = Trip | Pulse | Plant ESD | RU0001 |  | (Unit B)
114 | Air Cooler motor 2 vibration switch |  | VS-RU0001A-01A | 300-XS-4100A | Dry contact | DI | 1 = Vibration Alarm | Pulse | Field | RU0001 | NIS
115 | Air Cooler motor 3 vibration switch |  | VS-RU0001A-01B | 300-XS-4100A | Dry contact | DI | 1 = Vibration Alarm | Pulse | Field | RU0001 | NIS
116 | Air Cooler motor 2 vibration switch |  | VS-RU0001B-01A | 300-XS-4100A | Dry contact | DI | 1 = Vibration Alarm | Pulse | Field | RU0001 | NIS | (Unit B)
117 | Air Cooler motor 3 vibration switch |  | VS-RU0001B-01B | 300-XS-4100A | Dry contact | DI | 1 = Vibration Alarm | Pulse | Field | RU0001 | NIS | (Unit B)
118 | Condensor motor Fan 2 start command |  | XST-RU0001A-03A | 300-XS-4100A | Dry contact | DO | 1 = Start | Pulse | RU0001 | MCC
119 | Condensor motor Fan 2 stop command |  | XSP-RU0001A-03A | 300-XS-4100A | Dry contact | DO | 0= Stop | Pulse | RU0001 | MCC
120 | Condensor motor Fan 2 running status |  | XL-RU0001A-04A | 300-XS-4100A | Dry contact | DI | 1 = Running | Status | MCC | RU0001
121 | Condensor motor Fan 2 fault status |  | XF-RU0001A-04A | 300-XS-4100A | Dry contact | DI | 0= Fault | Status | MCC | RU0001
122 | Condensor motor Fan 3 start command |  | XST-RU0001A-03B | 300-XS-4100A | Dry contact | DO | 1 = Start | Pulse | RU0001 | MCC
123 | Condensor motor Fan 3 stop command |  | XSP-RU0001A-03B | 300-XS-4100A | Dry contact | DO | 0= Stop | Pulse | RU0001 | MCC
124 | Condensor motor Fan 3 running status |  | XL-RU0001A-04B | 300-XS-4100A | Dry contact | DI | 1 = Running | Status | MCC | RU0001
125 | Condensor motor Fan 3 fault status |  | XF-RU0001A-04B | 300-XS-4100A | Dry contact | DI | 0= Fault | Status | MCC | RU0001
126 | Condensor motor Fan 2 start command |  | XST-RU0001B-03A | 300-XS-4100A | Dry contact | DO | 1 = Start | Pulse | RU0001 | MCC |  | (Unit B)
127 | Condensor motor Fan 2 stop command |  | XSP-RU0001B-03A | 300-XS-4100A | Dry contact | DO | 0= Stop | Pulse | RU0001 | MCC |  | (Unit B)
128 | Condensor motor Fan 2 running status |  | XL-RU0001B-04A | 300-XS-4100A | Dry contact | DI | 1 = Running | Status | MCC | RU0001 |  | (Unit B)
129 | Condensor motor Fan 2 fault status |  | XF-RU0001B-04A | 300-XS-4100A | Dry contact | DI | 0= Fault | Status | MCC | RU0001 |  | (Unit B)
130 | Condensor motor Fan 3 start command |  | XST-RU0001B-03B | 300-XS-4100A | Dry contact | DO | 1 = Start | Pulse | RU0001 | MCC |  | (Unit B)
131 | Condensor motor Fan 3 stop command |  | XSP-RU0001B-03B | 300-XS-4100A | Dry contact | DO | 0= Stop | Pulse | RU0001 | MCC |  | (Unit B)
132 | Condensor motor Fan 3 running status |  | XL-RU0001B-04B | 300-XS-4100A | Dry contact | DI | 1 = Running | Status | MCC | RU0001 |  | (Unit B)
133 | Condensor motor Fan 3 fault status |  | XF-RU0001B-04B | 300-XS-4100A | Dry contact | DI | 0= Fault | Status | MCC | RU0001 |  | (Unit B)