## INDEX
Revision Index
Rev | 00 | 01 | 02 | 03 | 04 | 05 | Rev | 06 | 07 | 08 | 09
Sheet | [6 empty] | Sheet
1 | X
2 | X
3 | X
4 | X
5 | X
6 | X
7 | X
8 | X
9
10

## Unit A
Toase-ehe Park Sanati Gohar Ofogh Petrochemical Co. CONCEPTUAL, BASIC and DETAIL DESIGN ENGINEERING OF STYRENE PARK OFFSITE
Document Title: Istrument Cable List
|  | Document No.: | [9 empty] | Rev.00 | Page 3 of 4
COMPRESSOR RU0001A/B-C-01
No. | Service | Tag No. | Content of signal | SIGNAL Type | IS/NIS | Cable type | Cable size | Gland size | Cable Tag. | From | To | Length (Meter) | Remarks
1 | Compressor Suction pressure transmitter | PIT-RU0001A-01 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | PIT-RU0001A-01 | PIT-RU0001A-01 | JBD-A-RU0001A-01 | 10
2 | Discharge pressure transmitter | PIT-RU0001A-03 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | PIT-RU0001A-03 | PIT-RU0001A-03 | JBD-A-RU0001A-01 | 10
3 | Oil header Compressor pressure transmitter | PIT-RU0001A-02 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | PIT-RU0001A-02 | PIT-RU0001A-02 | JBD-A-RU0001A-01 | 10
4 | Upstream oil filter pressure transmitter | PIT-RU0001A-05 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | PIT-RU0001A-05 | PIT-RU0001A-05 | JBD-A-RU0001A-01 | 10
5 | Downstream oil filter pressure transmitter | PIT-RU0001A-06 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | PIT-RU0001A-06 | PIT-RU0001A-06 | JBD-A-RU0001A-01 | 10
6 | Pressure transmitter oil separator | PIT-RU0001A-04 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | PIT-RU0001A-04 | PIT-RU0001A-04 | JBD-A-RU0001A-01 | 10
7 | Compressor Suction temperature transmitter | TIT-RU0001A-01 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | TIT-RU0001A-01 | TIT-RU0001A-01 | JBD-A-RU0001A-01 | 10
8 | Oil Separator temperature transmitter | TIT-RU0001A-03 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | TIT-RU0001A-03 | TIT-RU0001A-03 | JBD-A-RU0001A-01 | 10
9 | Oil header compressor temperature transmitter | TIT-RU0001A-02 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | TIT-RU0001A-02 | TIT-RU0001A-02 | JBD-A-RU0001A-01 | 10
10 | Compressor slide valve position sensor | ZE-RU0001A-01 | 3-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | ZE-RU0001A-01 | ZE-RU0001A-01 | JBD-A-RU0001A-01 | 10
11 | Multi cable for JBD-A-RU0001A-01 |  |  |  | IS | (CU/XLPE/PVC/SWA/PVC) Blue | 15x2x1 mm² | M32 | JBD-A-RU0001A-01-UCP | JBD-A-RU0001A-01 | UCP-RU0001 | 400 m | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
12 | Chiller level transmitter | LIT-RU0001A-01 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | LIT-RU0001A-01 | LIT-RU0001A-01 | JBD-A-RU0001A-03 | 10
13 | Chiller level control valve | LV-RU0001A-01 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | LV-RU0001A-01 | LV-RU0001A-01 | JBD-A-RU0001A-03 | 10
14 | Multi cable for JBD-A-RU0001A-03 |  |  |  | IS | (CU/XLPE/PVC/SWA/PVC) Blue | 10x2x1 mm² | M25 | JBD-A-RU0001A-03-UCP | JBD-A-RU0001A-03 | UCP-RU0001 | 400 m | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
15 | Motor Winding U1 temperature element | PTC-RU0001A-13 | PTC / 2 wire | PTC
16 | Motor Winding U2 temperature element | PTC-RU0001A-14 | PTC / 2 wire | PTC
17 | Motor Winding V1 temperature element | PTC-RU0001A-15 | PTC / 2 wire | PTC
18 | Multi cable for COMP A. MAIN MOTOR PTC |  |  |  |  | (CU/XLPE/PVC/SWA/PVC) Gray | 3x2x1.5 mm² | M20 | RU0001A-M-01-MCC | RU0001A-M-01 | MCC | 200 m | 1-Cable and Gland will be supplied By Customer 2-Selected Cable shall be suitable for M20 Gland 3-Cable size shall be checked and confirmed by Customer
19 | Oil separator level switch | LS-RU0001A-01 | 24Vdc / **W | Digital | NIS | Type3 | 02Px1.5mm² | M20 | LS-RU0001A-01 | LS-RU0001A-01 | JBD-A-RU0001A-02 | 10
20 | Compressor capacity load Return solenoid valve | SOV-RU0001A-01D | 24Vdc / **W | Digital | NIS | Type 2 | 01Px2.5mm² | M20 | SOV-RU0001A-01D | SOV-RU0001A-01D | JBD-A-RU0001A-02 | 10
21 | Compressor capacity unload supply solenoid valve | SOV-RU0001A-01A | 24Vdc / **W | Digital | NIS | Type 2 | 01Px2.5mm² | M20 | SOV-RU0001A-01A | SOV-RU0001A-01A | JBD-A-RU0001A-02 | 10
22 | Compressor capacity load supply solenoid valve | SOV-RU0001A-01C | 24Vdc / **W | Digital | NIS | Type 2 | 01Px2.5mm² | M20 | SOV-RU0001A-01C | SOV-RU0001A-01C | JBD-A-RU0001A-02 | 10
23 | Compressor capacity unload Return solenoid valve | SOV-RU0001A-01E | 24Vdc / **W | Digital | NIS | Type 2 | 01Px2.5mm² | M20 | SOV-RU0001A-01E | SOV-RU0001A-01E | JBD-A-RU0001A-02 | 10
24 | Multi cable for JBD-A-RU0001A-02 |  | 24Vdc / **W | Digital | NIS | (CU/XLPE/PVC/SWA/PVC) Gray | 12x2.5 mm² | M32 | JBD-A-RU0001A-02-UCP | JBD-A-RU0001A-02 | UCP | 400 m | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
25
26 | Hot gas solenoid valve | SOV-RU0001A-03 | 24Vdc / **W | Digital | NIS | Type 2 | 01Px2.5mm² | M20 | SOV-RU0001A-03 | SOV-RU0001A-03 | JBD-A-RU0001A-04 | 10
27 | Evaporator oil drain line. | SOV-RU0001A-02 | 24Vdc / **W | Digital | NIS | Type 2 | 01Px2.5mm² | M20 | SOV-RU0001A-02 | SOV-RU0001A-02 | JBD-A-RU0001A-04 | 10
28 | Air Cooler motor 2 vibration switch | VS-RU0001A-01A | 24Vdc / **D | Digital | NIS | Type 2 | 01Px2.5mm² | M20 | VS-RU0001A-01A | VS-RU0001A-01A | JBD-A-RU0001A-04 | 10
29 | Air Cooler motor 3 vibration switch | VS-RU0001A-01B | 24Vdc / **D | Digital | NIS | Type 2 | 01Px2.5mm² | M20 | VS-RU0001A-01B | VS-RU0001A-01B | JBD-A-RU0001A-04 | 10
30 | Multi cable for JBD-A-RU0001A-04 |  | 24Vdc / **D**W | Digital | NIS | (CU/XLPE/PVC/SWA/PVC) Gray | 12x2.5 mm² | M32 | JBD-A-RU0001A-04-UCP | JBD-A-RU0001A-04 | UCP | 400 m | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
31 | Oil heater temp. control switch | TS-RU0001A-01A | 24Vdc / **D | Digital | NIS
32 | Oil heater Surface and box temp. control switch | TS-RU0001A-01B | 24Vdc / **D | Digital | NIS
33 | Multi cable for TS-RU0001A-01 |  | 24Vdc / **D | Digital | NIS | (CU/XLPE/PVC/SWA/PVC) Gray | 04Cx1.5mm² | M20 | TS-RU0001A-01-UCP | RU0001A-H-01 | UCP | 400 m | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
34 | LCP Switches |  | 24Vdc / **D | Digital | NIS | (CU/XLPE/PVC/SWA/PVC) Gray | 12Cx1.5 mm² | M25 | RU0001A-LCP-01-UCP | RU0001A-LCP-01 | UCP | 400 m | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
35 | LCP Switches |  | 24Vdc / **D | Digital | NIS | (CU/XLPE/PVC/SWA/PVC) Gray | 12Cx1.5 mm² | M25 | RU0001A-LCP-01-UCP | RU0001A-LCP-01 | UCP | 400 m | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
36 | LCP Switches |  | 24Vdc / **D | Digital | NIS | (CU/XLPE/PVC/SWA/PVC) Gray | 12Cx1.5 mm² | M25 | RU0001A-LCP-01-UCP | RU0001A-LCP-01 | UCP | 400 m | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
37 | LCP Lamps |  | 24Vdc / **D | Digital | NIS | (CU/XLPE/PVC/SWA/PVC) Gray | 12Cx2.5 mm² | M32 | RU0001A-LCP-01-UCP | RU0001A-LCP-01 | UCP | 400 m | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
38 | UCP to MCC (UCP Digital Output Command signals for main motor,oil pump, condenser :STT,STP, ETC) |  | 24Vdc / **D | Digital | NIS | (CU/XLPE/PVC/SWA/PVC) Gray | 15x2x1 mm² | M32 | Hold | RU0001A | MCC | 400 m | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
39 | MCC to UCP (UCP Digital Input Status signals for main motor,oil pump, condenser : Running,Fault, ETC) |  | 24Vdc / **D | Digital | NIS | (CU/XLPE/PVC/SWA/PVC) Gray | 15x2x1 mm² | M32 | Hold | MCC | RU0001A | 400 m | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
40 | UCP to MCC (UCP Digital Output Command signals for VFD condenser :STT,STP, ETC) |  | 24Vdc / **D | Digital | NIS | (CU/XLPE/PVC/SWA/PVC) Gray | 10x2x1 mm² | M25 | Hold | RU0001A | MCC | 400 m | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
41 | MCC to UCP (UCP Digital Input Status signals for VFD condenser : Running,Fault, ETC) |  | 24Vdc / **D | Digital | NIS | (CU/XLPE/PVC/SWA/PVC) Gray | 10x2x1 mm² | M25 | Hold | MCC | RU0001A | 400 m | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
42 | UCP to MCC (Analog signals for VFD condenser, Main motor current ) |  | 4 to 20mA / 2-wire | Analouge | NIS | (CU/XLPE/PVC/SWA/PVC) Gray | 02Px1 mm² | M20 | Hold | RU0001A | MCC | 400 m | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
43 | Communication with DCS |  |  | serial |  | Ethernet cable |  |  | Hold | UCP | DCS | 400 m
44 | ESD TRIP Signal | RU0001A-ESD-01 | 24Vdc / **D | Digital | NIS |  | 01Px2.5mm² |  | Hold | RU0001A-ESD-01 | UCP | 400 m | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
45 | UPS Power |  |  | Power cable |  | CU/XLPE/PVC (600/1000) Black | 02Cx4mm2 |  | UPS-RU0001A-1 | Instrument PDP | UCP | 400 m | By Customer
46 | Non-UPS Power |  |  | Power cable |  | CU/XLPE/PVC (600/1000) Black | 02Cx4mm2 |  | NUPS-RU0001A-1 | Instrument PDP | UCP | 400 m | By Customer

## Unit B
Toase-ehe Park Sanati Gohar Ofogh Petrochemical Co. CONCEPTUAL, BASIC and DETAIL DESIGN ENGINEERING OF STYRENE PARK OFFSITE
Document Title: Istrument Cable List
|  | Document No.: | [9 empty] | Rev.00 | Page 3 of 4
COMPRESSOR RU0001B-C-01
No. | Service | Tag No. | Content of signal | SIGNAL Type | IS/NIS | Cable type | Cable size | Gland size | Cable Tag. | From | To | Length (Meter) | Remarks
1 | Compressor Suction pressure transmitter | PIT-RU0001B-01 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | PIT-RU0001B-01 | PIT-RU0001B-01 | JBD-A-RU0001B-01 | 10
2 | Discharge pressure transmitter | PIT-RU0001B-03 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | PIT-RU0001B-03 | PIT-RU0001B-03 | JBD-A-RU0001B-01 | 10
3 | Oil header Compressor pressure transmitter | PIT-RU0001B-02 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | PIT-RU0001B-02 | PIT-RU0001B-02 | JBD-A-RU0001B-01 | 10
4 | Upstream oil filter pressure transmitter | PIT-RU0001B-05 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | PIT-RU0001B-05 | PIT-RU0001B-05 | JBD-A-RU0001B-01 | 10
5 | Downstream oil filter pressure transmitter | PIT-RU0001B-06 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | PIT-RU0001B-06 | PIT-RU0001B-06 | JBD-A-RU0001B-01 | 10
6 | Pressure transmitter oil separator | PIT-RU0001B-04 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | PIT-RU0001B-04 | PIT-RU0001B-04 | JBD-A-RU0001B-01 | 10
7 | Compressor Suction temperature transmitter | TIT-RU0001B-01 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | TIT-RU0001B-01 | TIT-RU0001B-01 | JBD-A-RU0001B-01 | 10
8 | Oil Separator temperature transmitter | TIT-RU0001B-03 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | TIT-RU0001B-03 | TIT-RU0001B-03 | JBD-A-RU0001B-01 | 10
9 | Oil header compressor temperature transmitter | TIT-RU0001B-02 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | TIT-RU0001B-02 | TIT-RU0001B-02 | JBD-A-RU0001B-01 | 10
10 | Compressor slide valve position sensor | ZE-RU0001B-01 | 3-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | ZE-RU0001B-01 | ZE-RU0001B-01 | JBD-A-RU0001B-01 | 10
11 | Multi cable for JBD-A-RU0001B-01 |  |  |  | IS | (CU/XLPE/PVC/SWA/PVC) Blue | 15x2x1 mm² | M32 | JBD-A-RU0001B-01-UCP | JBD-A-RU0001B-01 | UCP-RU0001 | 400 | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
12 | Chiller level transmitter | LIT-RU0001B-01 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | LIT-RU0001B-01 | LIT-RU0001B-01 | JBD-A-RU0001B-03 | 10
13 | Chiller level control valve | LV-RU0001B-01 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | LV-RU0001B-01 | LV-RU0001B-01 | JBD-A-RU0001B-03 | 10
14 | Multi cable for JBD-A-RU0001B-03 |  |  |  | IS | (CU/XLPE/PVC/SWA/PVC) Blue | 10x2x1 mm² | M25 | JBD-A-RU0001B-03-UCP | JBD-A-RU0001B-03 | UCP-RU0001 | 400 | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
15 | Motor Winding U1 temperature element | PTC-RU0001B-13 | PTC / 2 wire | PTC
16 | Motor Winding U2 temperature element | PTC-RU0001B-14 | PTC / 2 wire | PTC
17 | Motor Winding V1 temperature element | PTC-RU0001B-15 | PTC / 2 wire | PTC
18 | Multi cable for COMP A. MAIN MOTOR PTC |  |  |  |  | (CU/XLPE/PVC/SWA/PVC) Gray | 3x2x1.5 mm² | M20 | RU0001B-M-01-MCC | RU0001B-M-01 | MCC | 200 | 1-Cable and Gland will be supplied By Customer 2-Selected Cable shall be suitable for M20 Gland 3-Cable size shall be checked and confirmed by Customer
19 | Oil separator level switch | LS-RU0001B-01 | 24Vdc / **W | Digital | NIS | Type3 | 02Px1.5mm² | M20 | LS-RU0001B-01 | LS-RU0001B-01 | JBD-A-RU0001B-02 | 10
20 | Compressor capacity load Return solenoid valve | SOV-RU0001B-01D | 24Vdc / **W | Digital | NIS | Type 2 | 01Px2.5mm² | M20 | SOV-RU0001B-01D | SOV-RU0001B-01D | JBD-A-RU0001B-02 | 10
21 | Compressor capacity unload supply solenoid valve | SOV-RU0001B-01A | 24Vdc / **W | Digital | NIS | Type 2 | 01Px2.5mm² | M20 | SOV-RU0001B-01A | SOV-RU0001B-01A | JBD-A-RU0001B-02 | 10
22 | Compressor capacity load supply solenoid valve | SOV-RU0001B-01C | 24Vdc / **W | Digital | NIS | Type 2 | 01Px2.5mm² | M20 | SOV-RU0001B-01C | SOV-RU0001B-01C | JBD-A-RU0001B-02 | 10
23 | Compressor capacity unload Return solenoid valve | SOV-RU0001B-01E | 24Vdc / **W | Digital | NIS | Type 2 | 01Px2.5mm² | M20 | SOV-RU0001B-01E | SOV-RU0001B-01E | JBD-A-RU0001B-02 | 10
24 | Multi cable for JBD-A-RU0001B-02 |  | 24Vdc / **W | Digital | NIS | (CU/XLPE/PVC/SWA/PVC) Gray | 12x2.5 mm² | M32 | JBD-A-RU0001B-02-UCP | JBD-A-RU0001B-02 | UCP | 400 | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
25
26 | Hot gas solenoid valve | SOV-RU0001B-03 | 24Vdc / **W | Digital | NIS | Type 2 | 01Px2.5mm² | M20 | SOV-RU0001B-03 | SOV-RU0001B-03 | JBD-A-RU0001B-04 | 10
27 | Evaporator oil drain line. | SOV-RU0001B-02 | 24Vdc / **W | Digital | NIS | Type 2 | 01Px2.5mm² | M20 | SOV-RU0001B-02 | SOV-RU0001B-02 | JBD-A-RU0001B-04 | 10
28 | Air Cooler motor 2 vibration switch | VS-RU0001B-01A | 24Vdc / **D | Digital | NIS | Type 2 | 01Px2.5mm² | M20 | VS-RU0001B-01A | VS-RU0001B-01A | JBD-A-RU0001B-04 | 10
29 | Air Cooler motor 3 vibration switch | VS-RU0001B-01B | 24Vdc / **D | Digital | NIS | Type 2 | 01Px2.5mm² | M20 | VS-RU0001B-01B | VS-RU0001B-01B | JBD-A-RU0001B-04 | 10
30 | Multi cable for JBD-A-RU0001B-04 |  | 24Vdc / **D**W | Digital | NIS | (CU/XLPE/PVC/SWA/PVC) Gray | 12x2.5 mm² | M32 | JBD-A-RU0001B-04-UCP | JBD-A-RU0001B-04 | UCP | 400 | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
31 | Oil heater temp. control switch | TS-RU0001B-01A | 24Vdc / **D | Digital | NIS
32 | Oil heater Surface and box temp. control switch | TS-RU0001B-01B | 24Vdc / **D | Digital | NIS
33 | Multi cable for TS-RU0001B-01 |  | 24Vdc / **D | Digital | NIS | (CU/XLPE/PVC/SWA/PVC) Gray | 04Cx1.5mm² | M20 | TS-RU0001B-01-UCP | RU0001B-H-01 | UCP | 400 | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
34 | LCP Switches |  | 24Vdc / **D | Digital | NIS | (CU/XLPE/PVC/SWA/PVC) Gray | 12Cx1.5 mm² | M25 | RU0001B-LCP-01-UCP | RU0001B-LCP-01 | UCP | 400 | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
35 | LCP Switches |  | 24Vdc / **D | Digital | NIS | (CU/XLPE/PVC/SWA/PVC) Gray | 12Cx1.5 mm² | M25 | RU0001B-LCP-01-UCP | RU0001B-LCP-01 | UCP | 400 | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
36 | LCP Switches |  | 24Vdc / **D | Digital | NIS | (CU/XLPE/PVC/SWA/PVC) Gray | 12Cx1.5 mm² | M25 | RU0001B-LCP-01-UCP | RU0001B-LCP-01 | UCP | 400 | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
37 | LCP Lamps |  | 24Vdc / **D | Digital | NIS | (CU/XLPE/PVC/SWA/PVC) Gray | 12Cx2.5 mm² | M32 | RU0001B-LCP-01-UCP | RU0001B-LCP-01 | UCP | 400 | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
38 | UCP to MCC (UCP Digital Output Command signals for main motor,oil pump, condenser :STT,STP, ETC) |  | 24Vdc / **D | Digital | NIS | (CU/XLPE/PVC/SWA/PVC) Gray | 15x2x1 mm² | M32 | Hold | RU0001B | MCC | 400 | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
39 | MCC to UCP (UCP Digital Input Status signals for main motor,oil pump, condenser : Running,Fault, ETC) |  | 24Vdc / **D | Digital | NIS | (CU/XLPE/PVC/SWA/PVC) Gray | 15x2x1 mm² | M32 | Hold | MCC | RU0001B | 400 | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
40 | UCP to MCC (UCP Digital Output Command signals for VFD condenser :STT,STP, ETC) |  | 24Vdc / **D | Digital | NIS | (CU/XLPE/PVC/SWA/PVC) Gray | 10x2x1 mm² | M25 | Hold | RU0001B | MCC | 400 | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
41 | MCC to UCP (UCP Digital Input Status signals for VFD condenser : Running,Fault, ETC) |  | 24Vdc / **D | Digital | NIS | (CU/XLPE/PVC/SWA/PVC) Gray | 10x2x1 mm² | M25 | Hold | MCC | RU0001B | 400 | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer
42 | UCP to MCC (Analog signals for VFD condenser, Main motor current ) |  | 4 to 20mA / 2-wire | Analouge | NIS | (CU/XLPE/PVC/SWA/PVC) Gray | 02Px1 mm² | M20 | Hold | RU0001B | MCC | 400 | 1-Cable and Gland will be supplied By Customer 2-Cable size shall be checked and confirmed by Customer

## Type1
Toase-ehe Park Sanati Gohar Ofogh Petrochemical Co. CONCEPTUAL, BASIC and DETAIL DESIGN ENGINEERING OF STYRENE PARK OFFSITE
Document Title: Istrument Cable List
|  | Document No.: |  | Rev.00 | Page 3 of 4
1 | Item |  | 1
2 | DUTY |  | 2 Wire Transmitter,
3 | INSTALLATION LOCATION |  | OUTDOOR
4 | INSTALLATION METHOD |  | -
5 | AMBIENT TEMP MIN / MAX |  | -20 °C / 48 °C
6 | CABLE TECHNICAL DATA
7 | MAKE |  | LATER
8 | TYPE |  | As per EN50288-7
9 | CONDUCTORS |  | Stranded Copper - IEC 60228 class 2
10 | INSULATION |  | XLPE
11 | CORE / PAIR / TRIAD |  | Twisted Pair
12 | IDENTIFICATION |  | Black - white
13 | SCREENING |  | Collective Aluminium/Maylar tape + tinned copper drain wire
14 | BEDDING |  | PVC
15 | ARMOUR |  | Galvanised Steel Wire Armour (SWA)
16 | OUTER JACKET |  | PVC
17 | OUTER SHEATH COLOUR |  | Light Blue
18 | CROSS SECTION |  | 1.5 mm2
19 | NUMBER OF CORES / PARE / TRIADS |  | 1 Pair
20 | MAX. OPERATING VOLTAGE |  | 300 / 500 Volt
21 | MIN. OPERATING TEMPERATURE |  | -20 °C
22 | MAX. OPERATING TEMPERATURE |  | +60 °C
23 | CONDUCTOR MAXIMUM TEMPERATURE |  | +90 °C
24
25 | INNER SHEATH DIAMETER |  | Later
26 | OUTER SHEATH DIAMETER |  | Later
27
28 | FLAME RETARDANT |  | IEC60332-1-2 / IEC 60332-3-24 (cat.C)
29
30
31
32
33
34
35

## Type2
Toase-ehe Park Sanati Gohar Ofogh Petrochemical Co. CONCEPTUAL, BASIC and DETAIL DESIGN ENGINEERING OF STYRENE PARK OFFSITE
Document Title: Istrument Cable List
|  | Document No.: |  | Rev.00 | Page 3 of 4
1 | Item |  | 2
2 | DUTY |  | SOLENOID VALVE
3 | INSTALLATION LOCATION |  | OUTDOOR
4 | INSTALLATION METHOD |  | -
5 | AMBIENT TEMP MIN / MAX |  | -20 °C / 48 °C
6 | CABLE TECHNICAL DATA
7 | MAKE |  | LATER
8 | TYPE |  | As per EN50288-7
9 | CONDUCTORS |  | Stranded Copper - IEC 60228 class 2
10 | INSULATION |  | XLPE
11 | CORE / PAIR / TRIAD |  | Pair
12 | IDENTIFICATION |  | Black - white
13 | SCREENING |  | NA
14 | BEDDING |  | PVC
15 | ARMOUR |  | Galvanised Steel Wire Armour (SWA)
16 | OUTER JACKET |  | PVC
17 | OUTER SHEATH COLOUR |  | Gray
18 | CROSS SECTION |  | 2.5 mm2
19 | NUMBER OF CORES / PARE / TRIADS |  | 1 Pair
20 | MAX. OPERATING VOLTAGE |  | 300 / 500 Volt
21 | MIN. OPERATING TEMPERATURE |  | -20 °C
22 | MAX. OPERATING TEMPERATURE |  | +60 °C
23 | CONDUCTOR MAXIMUM TEMPERATURE |  | +90 °C
24
25 | INNER SHEATH DIAMETER |  | Later
26 | OUTER SHEATH DIAMETER |  | Later
27
28 | FLAME RETARDANT |  | IEC60332-1-2 / IEC 60332-3-24 (cat.C)
29
30
31
32
33
34

## Type3
Toase-ehe Park Sanati Gohar Ofogh Petrochemical Co. CONCEPTUAL, BASIC and DETAIL DESIGN ENGINEERING OF STYRENE PARK OFFSITE
Document Title: Istrument Cable List
|  | Document No.: |  | Rev.00 | Page 3 of 4
1 | Item |  | 3
2 | DUTY |  | Level Switches
3 | INSTALLATION LOCATION |  | OUTDOOR
4 | INSTALLATION METHOD |  | -
5 | AMBIENT TEMP MIN / MAX |  | -20 °C / 48 °C
6 | CABLE TECHNICAL DATA
7 | MAKE |  | LATER
8 | TYPE |  | As per EN50288-7
9 | CONDUCTORS |  | Stranded Copper - IEC 60228 class 2
10 | INSULATION |  | XLPE
11 | CORE / PAIR / TRIAD |  | Twisted Pair
12 | IDENTIFICATION |  | Black - white
13 | SCREENING |  | Collective Aluminium/Maylar tape + tinned copper drain wire
14 | BEDDING |  | PVC
15 | ARMOUR |  | Galvanised Steel Wire Armour (SWA)
16 | OUTER JACKET |  | PVC
17 | OUTER SHEATH COLOUR |  | Gray
18 | CROSS SECTION |  | 1.5 mm2
19 | NUMBER OF CORES / PARE / TRIADS |  | 2 Pair
20 | MAX. OPERATING VOLTAGE |  | 300 / 500 Volt
21 | MIN. OPERATING TEMPERATURE |  | -20 °C
22 | MAX. OPERATING TEMPERATURE |  | +60 °C
23 | CONDUCTOR MAXIMUM TEMPERATURE |  | +90 °C
24
25 | INNER SHEATH DIAMETER |  | Later
26 | OUTER SHEATH DIAMETER |  | Later
27
28 | FLAME RETARDANT |  | IEC60332-1-2 / IEC 60332-3-24 (cat.C)
29
30
31
32
33
34
35