## COVER
JAM ABS ¬ RUBBERS PLANT (BANDAR ASSALUYEH)
On-Off Valves Data Sheet
Contract No.: PPJPC-1400-17 | [6 empty] | JSC Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-007 | [5 empty] | Page: 1
Project no. : PPJP-99ME04 | [6 empty] | TCIM Doc. No.: **********
VENDOR Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-007
On-Off Valves Data Sheet
| VENDOR: | [5 empty] | KASRAVAND |  | VENDOR'S JOB: |  |  |  | 1082
| Purchase Order: | [5 empty] | PPJPC-1400-17 |  | Item: |  |  |  | ????
| Component: | [5 empty] | ????? |  | Equipment: |  |  |  | RTO
|  | Status Code | [5 empty] | Eng. |  | Dept. |  |  | Date
Comment status code:
|  |  | AP - Approved and released for Manufacture | [6 empty] | NC - No Comments
|  |  | CO - Not Approved | [6 empty] | AC - Approved with Comments
RE - Rejected
IMPORTANT: Permission to proceed does not constitute acceptance or approval of design details, calculations, analyses, test methods or materials developed or selected by the supplier and does not relieve supplier from full compliance with contractual obligation.
00 | 2023-10-30 |  |  | IFA |  | Issued For Approval |  |  |  |  | O.S | A.M | H.O
Rev | Date |  |  | Class |  | Status |  |  |  |  | Prepared | Checked | Approved | Prepared | Checked | Approved
[11 empty] | NOVA SYNERGY/KASRAVAND |  |  | TCM / JSC

## INDEX
JAM ABS ¬ RUBBERS PLANT (BANDAR ASSALUYEH)
On-Off Valves Data Sheet
Contract No.: PPJPC-1400-17 | [5 empty] | JSC Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-007 | [10 empty] | Page: 2
Project no. : PPJP-99ME04 | [5 empty] | TCIM Doc. No.: **********
VENDOR Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-007
PAGE | REVISION | [6 empty] | PAGE | REVISION | [6 empty] | PAGE |  | REVISION
| 0 | 1 | 2 | 3 | 4 | 5 | 6 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6
1 | [7 empty] | 79 | [7 empty] | 157 | bar: REVISION 0
2 | [7 empty] | 80 | [7 empty] | 158 | bar: REVISION 0
3 | [7 empty] | 81 | [7 empty] | 159 | bar: REVISION 0
4 | [7 empty] | 82 | [7 empty] | 160 | bar: REVISION 0
5 | [7 empty] | 83 | [7 empty] | 161 | bar: REVISION 0
6 | [7 empty] | 84 | [7 empty] | 162 | bar: REVISION 0
7 | [7 empty] | 85 | [7 empty] | 163 | bar: REVISION 0
8 | [7 empty] | 86 | [7 empty] | 164 | bar: REVISION 0
9 | [7 empty] | 87 | [7 empty] | 165 | bar: REVISION 0
10 | [7 empty] | 88 | [7 empty] | 166 | bar: REVISION 0
11 | [7 empty] | 89 | [7 empty] | 167 | bar: REVISION 0
12 | [7 empty] | 90 | [7 empty] | 168
13 | [7 empty] | 91 | [7 empty] | 169
14 | [7 empty] | 92 | [7 empty] | 170
15 | [7 empty] | 93 | [7 empty] | 171
16 | [7 empty] | 94 | [7 empty] | 172
17 | [7 empty] | 95 | [7 empty] | 173
18 | [7 empty] | 96 | [7 empty] | 174
19 | [7 empty] | 97 | [7 empty] | 175
20 | [7 empty] | 98 | [7 empty] | 176
21 | [7 empty] | 99 | [7 empty] | 177
22 | [7 empty] | 100 | [7 empty] | 178
23 | [7 empty] | 101 | [7 empty] | 179
24 | [7 empty] | 102 | [7 empty] | 180
25 | [7 empty] | 103 | [7 empty] | 181
26 | [7 empty] | 104 | [7 empty] | 182
27 | [7 empty] | 105 | [7 empty] | 183
28 | [7 empty] | 106 | [7 empty] | 184
29 | [7 empty] | 107 | [7 empty] | 185
30 | [7 empty] | 108 | [7 empty] | 186
31 | [7 empty] | 109 | [7 empty] | 187
32 | [7 empty] | 110 | [7 empty] | 188
33 | [7 empty] | 111 | [7 empty] | 189
34 | [7 empty] | 112 | [7 empty] | 190
35 | [7 empty] | 113 | [7 empty] | 191
36 | [7 empty] | 114 | [7 empty] | 192
37 | [7 empty] | 115 | [7 empty] | 193
38 | [7 empty] | 116 | [7 empty] | 194
39 | [7 empty] | 117 | [7 empty] | 195
40 | [7 empty] | 118 | [7 empty] | 196
41 | [7 empty] | 119 | [7 empty] | 197
42 | [7 empty] | 120 | [7 empty] | 198
43 | [7 empty] | 121 | [7 empty] | 199
44 | [7 empty] | 122 | [7 empty] | 200
45 | [7 empty] | 123 | [7 empty] | 201
46 | [7 empty] | 124 | [7 empty] | 202
47 | [7 empty] | 125 | [7 empty] | 203
48 | [7 empty] | 126 | [7 empty] | 204
49 | [7 empty] | 127 | [7 empty] | 205
50 | [7 empty] | 128 | [7 empty] | 206
51 | [7 empty] | 129 | [7 empty] | 207
52 | [7 empty] | 130 | [7 empty] | 208
53 | [7 empty] | 131 | [7 empty] | 209
54 | [7 empty] | 132 | [7 empty] | 210
55 | [7 empty] | 133 | [7 empty] | 211
56 | [7 empty] | 134 | [7 empty] | 212
57 | [7 empty] | 135 | [7 empty] | 213
58 | [7 empty] | 136 | [7 empty] | 214
59 | [7 empty] | 137 | [7 empty] | 215
60 | [7 empty] | 138 | [7 empty] | 216
61 | [7 empty] | 139 | [7 empty] | 217
62 | [7 empty] | 140 | [7 empty] | 218
63 | [7 empty] | 141 | [7 empty] | 219
64 | [7 empty] | 142 | [7 empty] | 220
65 | [7 empty] | 143 | [7 empty] | 221
66 | [7 empty] | 144 | [7 empty] | 222
67 | [7 empty] | 145 | [7 empty] | 223
68 | [7 empty] | 146 | [7 empty] | 224
69 | [7 empty] | 147 | [7 empty] | 225
70 | [7 empty] | 148 | [7 empty] | 226
71 | [7 empty] | 149 | [7 empty] | 227
72 | [7 empty] | 150 | [7 empty] | Appendix
73 | [7 empty] | 151
74 | [7 empty] | 152 | [7 empty] | Att. 1
75 | [7 empty] | 153 | [7 empty] | Att. 2
76 | [7 empty] | 154 | [7 empty] | Att. 3
77 | [7 empty] | 155 | [7 empty] | Att. 4
78 | [7 empty] | 156 | [7 empty] | Att. 5

## SOV-RU0001A C D E
JAM ABS ¬ RUBBERS PLANT (BANDAR ASSALUYEH)
On-Off Valves Data Sheet
Contract No.: PPJPC-1400-17 |  |  | JSC Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-007 |  | Page: 3
Project no. : PPJP-99ME04 |  |  | TCIM Doc. No.: **********
VENDOR Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-007
GENERAL | 1 | Tag Number |  | SOV-RU0001A-01A/C/D/E, SOV-RU0001B-01A/C/D/E
| 2 | Service |  | Solenoid valve for Capacity Control
| 3 | P&ID No. |  | EI027-HSE-VD-PR-PID-002 (2/7)
| 4 | Line No. |  | 1/2"-SS Tubing
| 5 | Quantity |  | 8
SOLENOID VALVE | 6 | Type |  | 2/2 Solenoid Valve
| 7 | Body size |  | 1/2" NPTF
| 8 | Type Conn. |  | Thread
| 9 | Material - Body |  | AISI 304 SS
| 10 | Material - Seat |  | Stainless steel, AISI type 316
| 11 | Material - Diaphragm |  | NA
| 12 | Operation Direct/Pilot |  | Direct
| 13 | Packless or Type Packed |  | Packed
| 14 | Fail position |  | Close
| 15 | Tight shut off
| 16 | Position indicator |  | No
| 17 | 2-Way Valve Opens/Close |  | Yes
| 18 | 3-Way |  | -
| 19 | Vent Port Opens/Close (De-Energized State) |  | -
| 20 | Press. Port Opens/Close (De-Energized State) |  | -
| 21 | 4-Way |  | -
| 22 | Press. to Cyl.1/Cyl.2 |  | -
| 23 | Exh. From Cyl.1/Cyl.2 |  | -
| 24 | Enclosure |  | IP - 65
| 25 | Electrical calssification |  | Eexd (IEC)
| 26 | Voltage / Hz |  | 24 VDC
| 27 | Style of Coil |  | Spring return/Insulation Class H
| 28 | Single or Double Coil |  | Single
| 29 | Rated current (A) |  | VTA
| 30 | Cable gland size |  | M20x1.5
AREA | 31 | Location |  | Outdoor
| 32 | Area classification |  | Zone 2 IIB, T3
| 33 | Ambient temperature |  | 5 / 48℃
| 34 | Humidity |  | Max 85%
SERVICE CONDITIONS | 35 | Fluid |  | LUBE OIL
| 36 | Operating Pressure |  | 22.5 bara
| 37 | Differential Pressure |  | 26 bar
| 38 | Design Pressure |  | 26 barg
| 39 | Temp. Norm |  | 60 °C
| 40 | Design Temperature |  | -29 / 100 °C
| 41 | Oper. Density |  | 1005 kg/m3
| 42 | Oper. Viscosity cp |  | 12
| 43 | Required Cv
| 44 | Valve Cv
45
PURCHASE | 46 | Manufacturer
| 47 | Model Number
Notes:
1. 3.1 Material Certification
2. Pressure test report (Hydro-test)
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED

## SOV-RU0001AB-02
JAM ABS ¬ RUBBERS PLANT (BANDAR ASSALUYEH)
On-Off Valves Data Sheet
Contract No.: PPJPC-1400-17 |  |  | JSC Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-007 |  | Page: 5
Project no. : PPJP-99ME04 |  |  | TCIM Doc. No.: **********
VENDOR Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-007
GENERAL | 1 | Tag Number |  | SOV-RU0001A-02 ,SOV-RU0001B-02
| 2 | Service |  | Oil Separator Recovery
| 3 | P&ID No. |  | EI027-HSE-VD-PR-PID-002 (3/7)
| 4 | Line No. |  | 1/2"-SS Tubing
| 5 | Quantity |  | 2
SOLENOID VALVE | 6 | Type |  | 2/2 Solenoid Valve
| 7 | Body size |  | 1/2" NPTF
| 8 | Type Conn. |  | Thread
| 9 | Material - Body |  | AISI 304 SS
| 10 | Material - Seat |  | Stainless steel, AISI type 304
| 11 | Material - Diaphragm |  | NA
| 12 | Operation Direct/Pilot |  | Direct
| 13 | Packless or Type Packed |  | Packed
| 14 | Fail position |  | Close
| 15 | Tight shut off
| 16 | Position indicator |  | No
| 17 | 2-Way Valve Opens/Close |  | Yes
| 18 | 3-Way |  | -
| 19 | Vent Port Opens/Close (De-Energized State) |  | -
| 20 | Press. Port Opens/Close (De-Energized State) |  | -
| 21 | 4-Way |  | -
| 22 | Press. to Cyl.1/Cyl.2 |  | -
| 23 | Exh. From Cyl.1/Cyl.2 |  | -
| 24 | Enclosure |  | IP - 65
| 25 | Electrical calssification |  | Eexd (IEC)
| 26 | Voltage / Hz |  | 24 VDC
| 27 | Style of Coil |  | Spring return/Insulation Class H
| 28 | Single or Double Coil |  | Single
| 29 | Rated current (A) |  | VTA
| 30 | Cable gland size |  | M20x1.5
AREA | 31 | Location |  | Outdoor
| 32 | Area classification |  | Zone 2 IIB, T3
| 33 | Ambient temperature |  | 5 / 48℃
| 34 | Humidity |  | Max 85%
SERVICE CONDITIONS | 35 | Fluid |  | LUBE OIL
| 36 | Operating Pressure |  | 20.2 bara
| 37 | Differential Pressure |  | 22 bar
| 38 | Design Pressure |  | 22 barg
| 39 | Temp. Norm |  | 73.5 °C
| 40 | Design Temperature |  | -29 / 100 °C
| 41 | Oper. Density |  | 1005 kg/m3
| 42 | Oper. Viscosity cp |  | 12
| 43 | Required Cv
| 44 | Valve Cv
45
PURCHASE | 46 | Manufacturer
| 47 | Model Number
Notes:
1. 3.1 Material Certification
2. Pressure test report (Hydro-test)
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED

## SOV-RU0001AB-06
JAM ABS ¬ RUBBERS PLANT (BANDAR ASSALUYEH)
On-Off Valves Data Sheet
Contract No.: PPJPC-1400-17 |  |  | JSC Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-007 |  | Page: 8
Project no. : PPJP-99ME04 |  |  | TCIM Doc. No.: **********
VENDOR Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-007
GENERAL | 1 | Tag Number |  | SOV-RU0001A-06,SOV-RU0001B-06
| 2 | Service |  | Hot Propane Gas from Oil Separator Header
| 3 | P&ID No. |  | EI027-HSE-VD-PR-PID-002 (6/7)
| 4 | Line No. |  | 1/2"-SS Tubing
| 5 | Quantity |  | 2
SOLENOID VALVE | 6 | Type |  | 2/2 Solenoid Valve
| 7 | Body size |  | 1/2" NPTF
| 8 | Type Conn. |  | Thread
| 9 | Material - Body |  | AISI 304 SS
| 10 | Material - Seat |  | AISI 304 SS
| 11 | Material - Diaphragm |  | NA
| 12 | Operation Direct/Pilot |  | Direct
| 13 | Packless or Type Packed |  | Packed
| 14 | Fail position |  | Close
| 15 | Tight shut off
| 16 | Position indicator |  | No
| 17 | 2-Way Valve Opens/Close |  | Yes
| 18 | 3-Way |  | -
| 19 | Vent Port Opens/Close (De-Energized State) |  | -
| 20 | Press. Port Opens/Close (De-Energized State) |  | -
| 21 | 4-Way |  | -
| 22 | Press. to Cyl.1/Cyl.2 |  | -
| 23 | Exh. From Cyl.1/Cyl.2 |  | -
| 24 | Enclosure |  | IP - 65
| 25 | Electrical calssification |  | Eexd (IEC)
| 26 | Voltage / Hz |  | 24 VDC
| 27 | Style of Coil |  | Spring return/Insulation Class H
| 28 | Single or Double Coil |  | Single
| 29 | Rated current (A) |  | VTA
| 30 | Cable gland size |  | M20x1.5
AREA | 31 | Location |  | Outdoor
| 32 | Area classification |  | Zone 2 IIB, T3
| 33 | Ambient temperature |  | 5 / 48℃
| 34 | Humidity |  | Max 85%
SERVICE CONDITIONS | 35 | Fluid |  | PROPANE
| 36 | Operating Pressure |  | 19.8 bara
| 37 | Differential Pressure |  | 22 bar
| 38 | Design Pressure |  | 22 barg
| 39 | Temp. Norm |  | 73.5 °C
| 40 | Design Temperature |  | -29 / 100 °C
| 41 | Oper. Density |  | 43.38 kg/m3
| 42 | Oper. Viscosity cp |  | 0.0106
| 43 | Required Cv
| 44 | Valve Cv
45
PURCHASE | 46 | Manufacturer
| 47 | Model Number
Notes:
1. 3.1 Material Certification
2. Pressure test report (Hydro-test)
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED

## SOV-RU0001AB-05
JAM ABS ¬ RUBBERS PLANT (BANDAR ASSALUYEH)
On-Off Valves Data Sheet
Contract No.: PPJPC-1400-17 |  |  | JSC Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-007 |  | Page: 9
Project no. : PPJP-99ME04 |  |  | TCIM Doc. No.: **********
VENDOR Doc. No.: PJ-80-KAS-IN-DSH-4100-0001-007
GENERAL | 1 | Tag Number |  | SOV-RU0001A-05,SOV-RU0001B-05
| 2 | Service |  | Hot Propane Gas to Compressor
| 3 | P&ID No. |  | EI027-HSE-VD-PR-PID-002 (6/7)
| 4 | Line No. |  | 1/2"-SS Tubing
| 5 | Quantity |  | 2
SOLENOID VALVE | 6 | Type |  | 2/2 Solenoid Valve
| 7 | Body size |  | 1/2" NPTF
| 8 | Type Conn. |  | Thread
| 9 | Material - Body |  | AISI 304 SS
| 10 | Material - Seat |  | AISI 304 SS
| 11 | Material - Diaphragm |  | NA
| 12 | Operation Direct/Pilot |  | Direct
| 13 | Packless or Type Packed |  | Packed
| 14 | Fail position |  | Close
| 15 | Tight shut off
| 16 | Position indicator |  | No
| 17 | 2-Way Valve Opens/Close |  | Yes
| 18 | 3-Way |  | -
| 19 | Vent Port Opens/Close (De-Energized State) |  | -
| 20 | Press. Port Opens/Close (De-Energized State) |  | -
| 21 | 4-Way |  | -
| 22 | Press. to Cyl.1/Cyl.2 |  | -
| 23 | Exh. From Cyl.1/Cyl.2 |  | -
| 24 | Enclosure |  | IP - 65
| 25 | Electrical calssification |  | Eexd (IEC)
| 26 | Voltage / Hz |  | 24 VDC
| 27 | Style of Coil |  | Spring return/Insulation Class H
| 28 | Single or Double Coil |  | Single
| 29 | Rated current (A) |  | VTA
| 30 | Cable gland size |  | M20x1.5
AREA | 31 | Location |  | Outdoor
| 32 | Area classification |  | Zone 2 IIB, T3
| 33 | Ambient temperature |  | 5 / 48℃
| 34 | Humidity |  | Max 85%
SERVICE CONDITIONS | 35 | Fluid |  | PROPANE + LUBE OIL
| 36 | Operating Pressure |  | 4.7 bara
| 37 | Differential Pressure |  | 22 bar
| 38 | Design Pressure |  | 22 barg
| 39 | Temp. Norm |  | -0.07 °C
| 40 | Design Temperature |  | -45 / 120 °C
| 41 | Oper. Density |  | 1005 kg/m3
| 42 | Oper. Viscosity cp |  | 12
| 43 | Required Cv
| 44 | Valve Cv
45
PURCHASE | 46 | Manufacturer
| 47 | Model Number
Notes:
1. 3.1 Material Certification
2. Pressure test report (Hydro-test)
3. Special design for MAYEKAWA compressor
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED