## Cover Page
Gachsaran Polymer Industries Company HDPE Plant
Equipment List for Refrigerator Package
P.O. No: GPIC-PT-MA-PO-000-3029 |  |  | VENDOR DOC. NO.: VD-GPIC-MA-3029-3029-0020 |  |  | Rev. | Page 1 of 3
01
Equipment List for Refrigerator Package
|  | Code 1 | No Comment / Approved
(Applicable Only for “For Review” and "For Approval" Documents) No comment and the document are released for Manufacturing.
|  | Code 2 | No Comment/ Approved with Note(s)
Vendor/Sub- Contractor shall correct, revise and resubmit the document. The document is released for Manufacturing if changes incorporated.
|  | Code 3 | Commented
Vendor/Sub-Contractor shall correct, revise and resubmit the document by the date specified. The document shall be revised under the Status of “R: Revised Issue”. All corrected documents shall be resubmitted before starting the Manufacturing Process.
|  | Code 4 | Not Accepted ( Rejected )
Vendor/Sub-Contractor shall re-work / re-design / re-specify the contents of the document according to the comments / reasons for rejection. All corrected documents shall be resubmitted before starting the manufacturing. Vendor/Sub-Contractor shall not proceed with subsequent works of Material Supply or Manufacturing until receiving Code1/Code2 or No Code from PURCHASER. Vendor/Sub-Contractor shall resubmit the document with the same revision within 6 working days after receiving comments.
|  | No Code | No Code
(Only for “For Information” Documents and “As Built DWGs”) Document has been submitted for PURCHASER's Information (FI). Consistency, completeness and correctness of document content is in Vendor/Sub-Contractor's responsibility.
Date:
Dept.:
Signature:
Above checking results by EIED shall in no way relieve Vendor of any liability, obligation and responsibility out of the purchase order and the mutual agreement in writing.
03
02
| 01 | 28.05.2025 | IFA | N.B | F.T | A.M
| 00 | 12.05.2025 | IFA | A.M | F.T | A.M
| Rev. | Date (DD.MMM.YY) | Purpose OF Issue | Prepared | Checked | Approved
Note on C41: Date should be added in a long format

## Index
Gachsaran Polymer Industries Company HDPE Plant
Equipment List for Refrigerator Package
P.O. No: GPIC-PT-MA-PO-000-3029 |  |  | VENDOR DOC. NO.: VD-GPIC-MA-3029-3029-0020 | [6 empty] | Rev | Page 2 of 3
01
REVISION INDEX
| Rev. Page | 00 | 01 | 02 | 03 | 04 | Rev. Page | 00 | 01 | 02 | 03 | 04
| 1 | X | X |  |  |  | 34
| 2 | X | X |  |  |  | 35
| 3 | X | X |  |  |  | 36
| 4 | [5 empty] | 37
| 5 | [5 empty] | 38
| 6 | [5 empty] | 39
| 7 | [5 empty] | 40
| 8 | [5 empty] | 41
| 9 | [5 empty] | 42
| 10 | [5 empty] | 43
| 11 | [5 empty] | 44
| 12 | [5 empty] | 45
| 13 | [5 empty] | 46
| 14 | [5 empty] | 47
| 15 | [5 empty] | 48
| 16 | [5 empty] | 49
| 17 | [5 empty] | 50
| 18 | [5 empty] | 51
| 19 | [5 empty] | 52
| 20 | [5 empty] | 53
| 21 | [5 empty] | 54
| 22 | [5 empty] | 55
| 23 | [5 empty] | 56
| 24 | [5 empty] | 57
| 25 | [5 empty] | 58
| 26 | [5 empty] | 59
| 27 | [5 empty] | 60
| 28 | [5 empty] | 61
| 29 | [5 empty] | 62
| 30 | [5 empty] | 63
| 31 | [5 empty] | 64
| 32 | [5 empty] | 65
| 33 | [5 empty] | 66

## PAGE 3
Gachsaran Polymer Industries Company HDPE Plant
Equipment List for Refrigerator Package
P.O. No: GPIC-PT-MA-PO-000-3029 |  |  | VENDOR DOC. NO.: VD-GPIC-MA-3029-3029-0020 |  |  |  | Rev | Page 3 of 3
01
EQUIPMENT
ROW | TAG NO. | DESCRIPTION |  | Q,TY | TECHNICAL DATA | MATERIAL | DESIGN TEMPERATURE |  | DESIGN PRESSURE
[7 empty] | (°C) |  | (barg)
1 | C-6101 A/B | Screw Compressor |  | 2 | Type= Screw Rated Flow= 27463 kg/h DP= 17.64 bar, Outlet Pressure= 20.2 bara BHP= 1098 kW, Power= 1250 kW | Casing= Low Temp Cast Steel (weldable) JIS G5152, SPCL1 Shaft= Cr-Mo Steel Forging JIS G3221, SFCM 930S | -28.89/120 |  | 23.8
2 | D-6101 | Oil Separator |  | 1 | OD x T.L T.L = 1371.6 x 3556.1 mm Operating Condition= 77.7 °C , 20.2 bara | Body= SA-516 GR70N | -45/125 |  | 25 + F.V
3 | D-6102 | Liquid Receiver |  | 1 | OD x T.L T.L = 914.4 x 7112 mm Operating Condition= 47.63 °C , 19.68 bara | Body= SA-516 GR70N | -45/125 |  | 25 + F.V
4 | E-6101 | Evaporator |  | 1 | Tema Type= BKU ID x L= 1168/1553 x 6096 mm, Area Per Shell= 549.6 m2 Heat Duty= 1759.3 kW, Tube No.= 541U | Shell= SA-516 GR70N Tube= SA-334 GR6 | Shell= -45/125 Tube= -45/125 |  | Shell= 25 + F.V Tube= 25 + F.V
5 | E-6102 | Oil Cooler |  | 1 | Tema Type= AEU ID x L= 356 x 4387.85 mm, Area Per Shell= 36.9 m2 Heat Duty= 366.2 kW, Tube No.= 69U | Shell= SA-516 GR70N Tube= SA-179 | Shell= -29/125 Tube= -29/190 |  | Shell= 28 + F.V Tube= 28
6 | E-6103 | Economizer |  | 1 | Tema Type= BEN ID x L= 381 x 2438.4 mm, Area Per Shell= 25.4 m2 Heat Duty= 394.9 kW, Tube No.= 180 | Shell= SA-516 GR70N Tube= SA-334 GR6 | Shell= -45/125 Tube= -45/125 |  | Shell= 25 + F.V Tube= 25 + F.V
7 | E-6104 | Condenser |  | 1 | Tema Type= BJM ID x L= 1070 x 6000 mm, Area Per Shell= 557.3 m2 Heat Duty= 2626.9 kW, Tube No.= 1598 | Shell= SA-516 GR70N Tube= SA-334 GR6 | Shell= -45/120 Tube= -29/190 |  | Shell=25 + F.V Tube= 28
8 | EH-6101 | Oil Heater |  | 1 | ID x SM-SM = 1371.6 x 3332 mm Operating Condition= 77.7 °C , 19 barg Heating Capacity= 9 kW | 304 SS | 125 |  | 25 + F.V
9 | F-6101 A/B | Oil Filter |  | 2 | Type= Cartridge OD x T.L T.L = 12" x 914.4 mm | Body= ASTM A312 Gr. 304L Element= Fiber / Stainless Steel | -28.9/121.1 |  | 28 + F.V
10 | F-6102 | Ppropylene Filter/Dryer |  | 1 | Type= Molecular Sieve OD x T.L T.L = 14" x 1016 mm | Body= SA-516 GR70N Element= Stainless Steel | -45/125 |  | 25.5 + F.V
11 | P-6101 A/B | Oil Pump |  | 2 | Type= Twin Screw Rated Flow= 241 LPM DP= 3.5, Outlet Pressure= 22.6 barg BHP= 5.1 kW, Power= 11 kW | Casing= Speroidal Graphite Iron JIS G5501, FC300 End Plates= Speroidal Graphite Iron JIS G5501, FC300 | 125 |  | 28