TABLE OF CONTENTS

1.	INTRODUCTION	3

1.1.	SCOPE OF DOCUMENT	3

1.2.	LIST OF ANNEXURES	3

1.3.	REFERENCE DOCUMENTS	4

1.4.	LIST OF ACRONYMS	5

2.	FAT PRE-REQUISITES	6

2.1.	HARDWARE FAT PRE-REQUISITES	6

2.2.	SOFTWARE FAT PRE-REQUISITES	6

3.	CONTROL HARDWARE	7

3.1.	BILL OF MATERIAL CHECKS	7

3.2.	GENERAL ARRANGEMENT CHECKS	9

3.3.	GROUND WIRING CHECKS	11

3.4.	POWER UP CHECKS	13

4.	REDUNDANCY CHECKS	16

4.1.	CONTROLLER HARDWARE REDUNDANCY	16

4.2.	POWER SUPPLY REDUNDANCY	18

5.	IO HARDWARE TESTS	20

5.1.1.	IO CHANNELS TEST	20

5.1.	C&E TESTING	23

5.2.	UCP’s COMMUNICATION TESTING	24

6.	APPLICATION TESTS	25

6.1.	GRAPHICS CHECKS	25

6.2.	OBJECT FUNCTINALITY TEST	26

6.2.1.	OBJECTS FUNCTIONALITY TEST	26

6.2.1.1.	ANALOG INPUT	26

6.2.1.2.	DIGITAL INPUT	27

6.2.1.3.	ANALOG OUTPUT	28

6.2.1.4.	OIL PUMP	29

6.2.1.5.	PID	30

7.	FAT COMPLETION CERTIFICATE	31

LIST OF TABLES

Table 1: Annexures	3

Table 2: Reference Documents	4

Table 3: List of Acronyms	5

Table 5: Bill of Material Checks - Objectives	7

Table 6: Bill of Material Checks	8

Table 7: General Arrangement Checks - Objectives	9

Table 8: General Arrangement Checks – Detailed Procedure	9

Table 9: General Arrangement Checks	10

Table 10: Ground Wiring Checks - Objectives	11

Table 11: Ground Wiring Checks	12

Table 12: Power up Checks - Objectives	14

Table 13: Power up Checks	15

Table 19: Controller Hardware Redundancy Checks - Objectives	17

Table 20: Controller Hardware Redundancy Checks	17

Table 21: Power Supply Redundancy Checks - Objectives	18

Table 22: Power Supply Redundancy Checks	19

Table 23: IO Channel Checks - Objectives	21

Table 24:  IO Channel Checks	22

Table 27: C&E Testing Objective	23

Table 28: C&E Testing	23

Table 29: Serial Communication Checks - Objectives	24

Table 30: Serial Communication Checks	24

Table 31: Graphics Verification	25

Table 32: DCS Analog Input Functionality Test	26

Table 33: DCS Digital Input Functionality Test	27

Table 34: DCS Analog Output Functionality Test	28

Table 36: Process Pump Functionality Test	29

Table 37: PID Object Functionality Test	30

INTRODUCTION

Gachsaran Polymer Industries Company (GPIC) has awarded the project of Gachsaran HDPE Plant REFRIGERATION UNIT to HSE Group the control system and the scope include engineering, design, implementation & testing (FAT).

SCOPE OF DOCUMENT

This document outlines the objective, procedures, prerequisites, forms and other requirements to carry out Factory Acceptance Test for this project. The purpose of FAT is to verify the compliance of the equipment and software supplied by HSE Group to the requirements and specifications of the client. The FAT will be conducted in order to verify system integration, hardware functionality, software integration and configuration.

In addition, Hardwired IO testing and wiring shall be carried out during the FAT, the purpose of which shall be to verify the functionality of the hardware as per requirements of the client.

Any incomplete work or non-conformances detected during the FAT will be noted on a punch list. Outstanding items shall be cleared before shipment.

Upon successful completion of the FAT, authorized representatives of customer will sign the certificate of acceptance in the space provided. (If required)

LIST OF ANNEXURES

| Annexure | Details |
| --- | --- |
| Annexure A | Modification Control |
| Annexure B | FAT Punch List |

Table 1: Annexures

REFERENCE DOCUMENTS

| Sr. | Reference Documents | Document Number |
| --- | --- | --- |
|  | Control System Block Diagram | VD-GPIC-MA-3029-3029-0050 |
|  | I/O List | VD-GPIC-MA-3029-3029-0045 |
|  | PLC Circuit Wiring Drawing | VD-GPIC-MA-3029-3029-0048 |
|  | C&E Diagram | VD-GPIC-MA-3029-3029-0018 |

Table 2: Reference Documents

LIST OF ACRONYMS

| Acronym | Words/Phrase Represented by Acronym |
| --- | --- |
| AI | Analog Input |
| AO | Analog Output |
| CPU | Central Processing Unit |
| DCS | Distributed Control System |
| DI | Digital Input |
| DO | Digital Output |
| FAT | Factory Acceptance Test |
| HMI | Human Machine Interface |
| HW | Hardware |
| I/O | Input / Output |
| SW | Software |

Table 3: List of Acronyms

FAT PRE-REQUISITES

All documents listed in the Reference Documents section will be available prior to the execution of FAT.

HARDWARE FAT PRE-REQUISITES

The following tools shall be made available:

- Digital Multi-meters with calibration certificate.

- Analog Current Simulator with calibration certificate.

The following activities shall be completed prior to FAT:

- The panels will be placed inside Panel Workshop for all access/ testing activities.

- Power cables will be run and terminated into the panels.

- Communication cables will be installed and terminated. (excluding communication cables for third party systems).

SOFTWARE FAT PRE-REQUISITES

The following software’s will be installed and properly configured on EWS:

- TIA Portal V17

- ModScan

CONTROL HARDWARE

BILL OF MATERIAL CHECKS

| OUTLINE | : | All the supplied hardware is complete in terms of Quantity and no functionally required equipment/ item is missing. |
| --- | --- | --- |
| OBJECTIVE | : | The purpose of this test is to verify that all the supplied hardware type and quantity is as per Bill of Material in Panel General Arrangement drawings. |
| REFERENCE | : | Panel General Arrangement Drawings: VD-GPIC-MA-3029-3029-0048 |
| PROCEDURE | : | For each item/equipment installed in the control panel, the model no. and quantity shall be verified as per the respective General Arrangement Drawings. |
| CRITERIA | : | There should not be any discrepancies with respect to the installed panel hardware BOM. |

Table 5: Bill of Material Checks - Objectives

The BOM Checks will be carried out for the following:

| Description | Panel No. | Pass/ Fail | Checked/Verified By | Remarks |
| --- | --- | --- | --- | --- |
| Bill of Material for UCP Cabinet |  |  |  |  |

Table 6: Bill of Material Checks

GENERAL ARRANGEMENT CHECKS

| OUTLINE | : | Panel Fabrications as per Panel General Layout and Drawings |
| --- | --- | --- |
| OBJECTIVE | : | The purpose of this test is to verify that all the control hardware is installed in the cabinets as per customer approved Panel General Arrangement Drawings |
| REFERENCE | : | Panel General Arrangement Drawings: VD-GPIC-MA-3029-3029-0048 |
| PROCEDURE | : | refer to Panel General Arrangement drawing to verify that the control system hardware, terminal blocks, panel accessories have been installed at respective locations and dimensions inside the cabinet |
| CRITERIA | : | There should not be any discrepancies with respect to manufactured control cabinets and General Arrangement Drawings |

Table 7: General Arrangement Checks - Objectives

| Sr.No. | Detailed Test Procedure |
| --- | --- |
|  | Check the cabinet from outside and inside for any damages, scratches or un-necessary drillings / cuttings. |
|  | Check the dimensions of the cabinet and verify the material of the panel. |
|  | Check the lock and handle of the door for their proper working and spare keys. |
|  | Check tagging/nameplates of the cabinet both internal and external. |
|  | Check if all Power Supplies, Processor, I/O and communication modules inside the panel are placed according to the general arrangement drawings |
|  | Check type, quantity, tagging and placement of all terminal blocks |
|  | Check type, quantity, rating, tagging and placement of all circuit breakers. |
|  | Check type, quantity, tagging and placement of enclosure light(s) and outlet socket(s). |
|  | Check type, quantity, tagging and placement of all communication devices |
|  | Check panel color, thickness, document pocket holder |

Table 8: General Arrangement Checks – Detailed Procedure

The General Arrangement Checks will be carried out for the following Panels:

| Description | Panel No. | Pass/ Fail | Checked/Verified By | Remarks |
| --- | --- | --- | --- | --- |
| GA Check UCP Cabinet |  |  |  |  |

Table 9: General Arrangement Checks

GROUND WIRING CHECKS

| OUTLINE | : | All equipment inside the panel has been properly connected to appropriate ground as per Power distribution drawings. |
| --- | --- | --- |
| OBJECTIVE | : | The purpose of this test is to ensure that all panels’ internal equipment, panel body, light fan etc. has been properly grounded with safety ground bars provided in each panel. |
| REFERENCE | : | Panel Wiring Drawing: VD-GPIC-MA-3029-3029-0048 |
| PROCEDURE | : | following items will be checked for continuity - Each Power Supply GND Terminal to Ground - Each Panel Body to Ground. - Each Fan, Light and Power Socket to Ground - Isolation between different earth bars (IS/NIS/panel earth) |
| CRITERIA | : | There should not be any discrepancies with respect to grounding specification given on Power distribution and IO Wiring drawings and actual panel wiring done. |

Table 10: Ground Wiring Checks - Objectives

Grounding checks will be carried out for the following Panels:

| Description | Panel No. | Pass/ Fail | Checked/Verified By | Remarks |
| --- | --- | --- | --- | --- |
| GA Check for UCP Cabinet |  |  |  |  |

Table 11: Ground Wiring Checks

POWER UP CHECKS

| OUTLINE | : | Steady Power is supplied to all Panel Equipment and Accessories |
| --- | --- | --- |
| OBJECTIVE | : | The purpose of this test is to ensure that as power is applied to control system cabinet, all the installed panel equipment powers up normally with no circuit breaker trips |
| REFERENCE | : | Panel Wiring Drawing: VD-GPIC-MA-3029-3029-0048 |
| PROCEDURE | : | following items will be checked for Power up: - Make sure continuity test has been performed. - Turn OFF the main circuit breaker. - Open/Turn off all fuse terminals/Breakers for AC & DC distribution - Turn off power switches on all equipment/devices. - Apply AC power to the incoming power terminals. - Check the AC voltages at the main circuit breaker input - Live to Neutral should be 110 V - Turn ON main circuit breakers one by one. - Check AC voltages at the AC Distribution Breakers input. - Turn ON AC distribution circuit breakers one by one. - Check the AC voltages at the AC bulk Power Supplies Input. - Check the 24VDC at Bulk Power Supplies Output and Redundancy Modules - Check 24VDC at DC Distribution TB’s incoming. - Plug in the DC distribution TB’s one by one and check the DC voltage at corresponding DC equipment input. - Verify the wiring colors and labels as per power distribution and IO wiring drawings. |
| CRITERIA | : | There should not be any discrepancies in power up procedure. No circuit breaker should trip and all the power supplies, fans, and lights should function normally |

Table 12: Power up Checks - Objectives

Power up checks will be carried out for the following Panels:

| Description | Panel No. | Pass/ Fail | Checked/Verified By | Remarks |
| --- | --- | --- | --- | --- |
| Power Check for UCP Cabinet |  |  |  |  |

Table 13: Power up Checks

REDUNDANCY CHECKS

CONTROLLER/IO MODULE HARDWARE REDUNDANCY

| OUTLINE | : | All controllers and associated redundancy hardware are fully redundant with auto controller switch over at fault in primary controller. Critical IO module shall be fully redundant |
| --- | --- | --- |
| OBJECTIVE | : | The purpose of this test is to verify that the provided controller’s hardware/IO modules is redundant and auto-switch over occurs at fault in primary controller. |
| REFERENCE | : |  |
| PROCEDURE | : | following items will be checked for Controller Redundancy: - Remove Controller-A from rack - Controller-B will take over without any loss of data on application and will be Primary/Master Controller. - Insert back Controller-A in the rack - Controller-A will be Secondary/Standby. Check on application. - Remove Controller-B from rack - Controller-A will take over without any loss of data on application and will be Primary/Master Controller. Check on application. - Insert back Controller-B in the rack - Controller-B will be Secondary/Standby. Check on application. - Disconnect IO module A and check output at PLC - Disconnect IO module B and check output at PLC |
| CRITERIA | : | There should not be any discrepancies with the provided procedure. |

Table 19: Controller Hardware Redundancy Checks - Objectives

Controller’s hardware redundancy checks will be carried out for the following Panels:

| Description | Node No. | Pass/ Fail | Checked/Verified By | Remarks |
| --- | --- | --- | --- | --- |
| Controller Hardware Redundancy Check for UCP-Controller-A | UCP-Controller-A |  |  |  |
| Controller Hardware Redundancy Check for UCP-Controller-B | UCP-Controller-B |  |  |  |

Table 20: Controller Hardware Redundancy Checks

POWER SUPPLY REDUNDANCY

| OUTLINE | : | All power supplies provided are redundant and should be able to provide uninterrupted supply to the hardware. |
| --- | --- | --- |
| OBJECTIVE | : | The purpose of this test is to verify that the provided power supplies are redundant and auto switch over of load occurs. |
| REFERENCE | : |  |
| PROCEDURE | : | following items will be checked for Power Supply Redundancy. The test will be repeated for each pair of power supplies: - Make sure both supplies are connected to AC distribution terminal and turned ON. - Cut off the AC power supply to the first power supply using Circuit Breaker. - No glitch shall be observed and all the equipment shall remain functional. - Restore the AC power to the first power supply. - Now repeat the above with second power supply. - Under both cases the DC equipment (connected at output of power supply) shall remain operational. |
| CRITERIA | : | There should not be any discrepancies with the provided procedure. |

Table 21: Power Supply Redundancy Checks - Objectives

The following cabinets will be checked for the given procedure:

| Description | Panel No. | Pass/ Fail | Checked/Verified By | Remarks |
| --- | --- | --- | --- | --- |
| Power Supplies Redundancy Check for UCP Cabinet |  |  |  |  |

Table 22: Power Supply Redundancy Checks

IO HARDWARE TESTS

IO CHANNELS TEST

| OUTLINE | : | All the supplied IO module channels are functional. |
| --- | --- | --- |
| OBJECTIVE | : | The purpose of the test is to verify that all the IO channels in the supplied IO module are operational and applied field signals are readable to controller |
| REFERENCE | : | I/O List: VD-GPIC-MA-3029-3029-0045 Panel Wiring Drawing: VD-GPIC-MA-3029-3029-0048 |
| PROCEDURE | : | Note: IO Testing shall be carried out on the basis of IO List Download the application in the controller. Open the respective screen for the IO in the Operator workplace. Locate the IO and proceed with the following procedure: Analog Input - For each AI, locate the rack/slot/channel assignment from IO list. Identify the engineering signal limits as well. - Refer to module wiring and locate the corresponding field terminal blocks - Connect a 4-20mA signal generator to the field terminals. - Vary the input current from 4mA to 20mA in steps of 4mA. - Observe the value of corresponding tag on the screen. The value should vary from 0% to 100% in steps of 25% of engineering limits. - Reduce the signal from 20mA to 4mA to observe the engineering value decreasing accordingly. Digital Input - For each DI, locate the rack/slot/channel assignment from IO list. Locate the associated field terminal blocks from module wiring drawing. - Using a jumper wire, short the field input terminals. - The corresponding tag on the screen should change from binary 0 to 1. Remove the jumper, the signal should change back to 0. Digital Output - For each DO, locate the rack/slot/channel assignment from IO list and locate the associated field terminal blocks from module wiring drawing. - Connect a multi-meter to the field output terminals. - Force the output tag as specified in the IO List from FALSE to TRUE. The multi-meter should read 24VDC. Remove the IO force and observe the reading changes back to 0VDC. Analog Output - For each AO, locate the rack/slot/channel assignment from IO list. - Connect a multi-meter to the field output terminals. - Locate the corresponding PID controller associated with the AO on the screen. - Put the PID controller in Manual mode. Change control variable output from 0-100%. Observe that the output varies from 4-20mA. |
| CRITERIA | : | All the IOs in the system respond to input signals inside controller database and generate desired outputs on forcing. |

Table 23: IO Channel Checks - Objectives

IO Channel checks will be carried out for the following Panels:

| Description | Panel No. | Pass/ Fail | Checked/Verified By | Remarks |
| --- | --- | --- | --- | --- |
| IO Channels Check for UCP Cabinet |  |  |  |  |

Table 24:  IO Channel Checks

  - C&E TESTING

| OBJECTIVE | : | The purpose of the test is to verify the C&E. |
| --- | --- | --- |
| REFERENCE | : | C&E : VD-GPIC-MA-3029-3029-0018 |
| PROCEDURE | : | For each effect, put all causes in Maintenance Bypass, then remove bypass from each cause one by one and simulate its alarm state as per C&E. |
| CRITERIA | : | All effects should trip as per C&E. |

Table 27: C&E Testing Objective

| Description | Pass/ Fail | Checked/Verified By | Remarks |
| --- | --- | --- | --- |
| C&E Testing |  |  |  |

Table 28: C&E Testing

UCP’s COMMUNICATION TESTING

| OUTLINE | : | The Modbus TCP communication between UCP and DCS is functional |
| --- | --- | --- |
| OBJECTIVE | : | The purpose of the test is to verify that Modbus TCP communication between UCP and DCS is functional. |
| REFERENCE | : | UCP’s Modbus IO List |
| PROCEDURE | : | connect a system carrying Modscan application to Switch and proceed as following: - Set the analog and digital input/output parameters on the PLC, then verify their respective values using ModScan. |
| CRITERIA | : | All the tested signals inside the ModScan database respond to the data changes made within the PLC application. |

Table 29: Serial Communication Checks - Objectives

UCP’s communication Checks will be carried out for the following:

| Description | Panel No. | Pass/ Fail | Checked/Verified By | Remarks |
| --- | --- | --- | --- | --- |
| Client DCS |  |  |  |  |

Table 30: Serial Communication Checks

APPLICATION TESTS

Below given tests will be performed to verify all aspects are as per information provided by client.

GRAPHICS CHECKS

The purpose of this test is to verify HMI screens and the physical layout of HMI screens as per PID.

| Description | Pass/ Fail | Checked/Verified By | Remarks |
| --- | --- | --- | --- |
| Verify the general look and feel for operator environment |  |  |  |
| Verify Graphics Screen Count is same as per provided P&ID’s and C&E. |  |  |  |
| Check Graphics General Outlook including Object Placement, screen background color, text and pipe color coding. |  |  |  |
| Check Graphics Navigation |  |  |  |
| Check trends |  |  |  |

Table 31: Graphics Verification

OBJECT FUNCTINALITY TEST

The purpose of this test is to verify software functionality of all Process, which are controlled and/or monitored by UCP system.

OBJECTS FUNCTIONALITY TEST

The Object Functionality Test for Process Objects used in UCP is explained below:

ANALOG INPUT

The following procedure is followed for Analog Input Object Functionality Test:

| Description | Pass/ Fail | Checked/Verified By | Remarks |
| --- | --- | --- | --- |
| Verify each Process Analog Input as per IO List is present. |  |  |  |
| Verify the Tag Name and Engineering Units for all Analog Inputs |  |  |  |
| For any AI with H Alarm, connect 4-20mA signal generator with marshalling TB’s and verify the alarm status on HMI Screen & Alarm List |  |  |  |
| For any AI with L Alarm, connect 4-20mA signal generator with marshalling TB’s and verify the alarm status on HMI Screen & Alarm List. |  |  |  |
| For any AI with any active alarm state, acknowledge the alarm and verify that alarm ack in Alarm list. |  |  |  |
| For any AI with any active alarm state, normalize the process value and verify that Alarm List shows Alarm Returned indication. |  |  |  |
| For any AI with Alarm Returned indication, acknowledge the alarm and verify that alarm state is cleared. |  |  |  |

Table 32: DCS Analog Input Functionality Test

DIGITAL INPUT

The following procedure is followed for Digital Input Object Functionality Test:

| Description | Pass/ Fail | Checked/Verified By | Remarks |
| --- | --- | --- | --- |
| Verify each Process Digital Input as per IO List is present. |  |  |  |
| Verify the Tag Name for all Digital Inputs |  |  |  |
| Jumper the marshalling TB’s for Normal state and verify the ‘Green’ color indication on HMI. |  |  |  |
| Remove the jumper and verify the ‘Red’ color indication with active alarm status on HMI Screen & Alarm List |  |  |  |
| For any DI with active alarm state, acknowledge the alarm and verify that alarm ack. |  |  |  |
| For any DI with active alarm state, normalize the DI and verify that Alarm List shows Alarm Returned indication. |  |  |  |
| For any DI with Alarm Returned indication, acknowledge the alarm and verify that alarm state is cleared. |  |  |  |

Table 33: DCS Digital Input Functionality Test

ANALOG OUTPUT

The following procedure is followed for Analog Output Object Functionality Test:

| Description | Pass/ Fail | Checked/Verified By | Remarks |
| --- | --- | --- | --- |
| Verify each Process Analog Output as per IO List is present. |  |  |  |
| Verify the Tag Name and Engineering Units for all Analog Outputs |  |  |  |
| For an AO, put respective PID in Manual and force the output and verify the % open/close of Control Valve (AO) and value displayed on HMI. Also verify the mA from marshalling TB’s. |  |  |  |

Table 34: DCS Analog Output Functionality Test

OIL PUMP

The following procedure is followed for Process Pump Object Functionality Test:

| Description | Pass/ Fail | Checked/Verified By | Remarks |
| --- | --- | --- | --- |
| Verify each Oil Pump as per IO List is present in Graphics. |  |  |  |
| Verify the Tag Name for each Process Pump. |  |  |  |
| Put pump in Remote by putting jumper for the respective marshaling TB. - From faceplate, put pump in auto mode and check pump start/stop from control narrative. - From faceplate, put pump in Manual mode and check pump start/stop from faceplate. - Put pump in Local by removing jumper for the respective marshaling TB. - Change feedback status from Marshalling TB’s and verify on HMI. |  |  |  |
| Verify that Oil Pumps lead lag as per control philosophy |  |  |  |

Table 36: Process Pump Functionality Test

PID

The following procedure is followed for PID Object Functionality Test:

| Description | Pass/ Fail | Checked/Verified By | Remarks |
| --- | --- | --- | --- |
| Verify each PID object in Graphics for all. |  |  |  |
| Verify the Tag Name for each PID object. |  |  |  |
| Enable Manual Mode of PID and verify that controlled Output field is editable. |  |  |  |
| Enable Auto Mode and for reverse action of PID object; verify the cases: - When PV> SP, the Control Output starts decreasing to ‘0’ until PV becomes equal to SP. - When PV< SP, the Control Output increases until PV becomes equal to SP. |  |  |  |
| Enable Auto Mode and for direct action of PID object; verify the cases: - When PV< SP, the Control Output starts decreasing to ‘0’ until PV becomes equal to SP. - When PV> SP, the Control Output increases until PV becomes equal to SP. |  |  |  |

Table 37: PID Object Functionality Test

FAT COMPLETION CERTIFICATE

| Project Title: | Refrigeration Package |
| --- | --- |
| Vendor: | HSE. |
| Vendor Project Code: |  |
| End User: | Gachsaran Polymer Industries Company (GPIC) |
| End User Project Code: |  |
| FAT Period: |  |

DECLARATION:

It is hereby declared that Hardware FAT of “Refrigeration Package PLC Cabinet Hardware, Installation, Integration and Inspection” project for Gachsaran Polymer Industries Company (GPIC) Limited has been completed successfully as per FAT held in HSE and all outstanding items have been addressed and resolved as per HSE comments and recommendations.

COMMENTS:

__________________________________________________________________________________

__________________________________________________________________________________

__________________________________________________________________________________

__________________________________________________________________________________

AUTHORISED REPRESENTATIVES:

HSE 		                                 GPIC

Name:		      __________________	                    ___________________

Title: 		      __________________	                    ___________________

Signature: 		      __________________	                    ___________________

Date: 		      __________________	                    ___________________