## Table 1
|  | Gachsaran Polymer Industries Company HDPE Plant | [6 empty] | SHEET: 1 OF 5
DATE: 21.Jan.2025
P.O. No: GPIC-PT-MA-PO-000-3029 |  | Inspection And Test Plan (ITP) for Refrigerator Package | [6 empty] | REV.: 00
P.O. Title: Refrigeration Unit Package |  | VENDOR DOC. NO.: VD-GPIC-MA-3029-3029-0003 | [6 empty] | BY : MO
ITEM NO(S).: PK6101
1 | SCOPE | This Inspection and Test plan covers all activtiies that will be carrived out in design and farbrication of equipment.
2 | LEGEND OF THE TECHNICAL SURVEILLANCE | 1) (H)= INSPECTION NOTIFICATION will be issued by manufacturer and inspection shall be performed at presence of notified party. Next farbication stage is subject to acceptance of inspection. Vendor must notify parties (see inspection activtiy) of the defidcated inspection activity at least fifteen (15) days in advance.
2) (SW)=10% OF TYPE/LOT WITNESSED. Action performed only on a certain number of pieces.
3) (W)=WITNESSING. The Supplier shall inform the NOTIFIED PARTY of the date of the activity and the NOTIFIED PARTY reserves the right to witness the test. If the test is conducted at the notified date, the Supplier may proceed with the subsequent phase, even if the NOTIFIED did not witness the test.
4) (R/A)=REVIEW OF TECHNICAL DOCUMENTS BEFORE COMMENCEMENT OF CONSTRUCTION. The technical documents shall be reviewed and approved before the commencement of construction
5) (R )=REVIEW OF DOCUMENTS. Materials certificates, statement of compliance and reports of inspection and tests conducted by the Supplier shall be revised to assess their conformance with the requirements specified in the Code and Standards, Specifications and/or Purchase Order.
6) (D) = Vendor Inspection
3 | Abbreviations | O= Owner (GPIC) C= Contractor (EIED) V= Vendor (HSE/RHINE) SV = Sub Vendor TPI = Third Party Inspection on behalf of owner
Item No. | Inspection Description | References / Specifications / Codes | Verifying Document | Acceptance Criteria | INSPECTION ACTIVITY |  |  |  | REMARKS | R E V
[5 empty] | SUB-VENDOR (SV) | VENDOR (V) | EIED(C) | O/TPI
A PROJECT PREPARATION
A1 | PRE INSPECTION MEETING |  |  |  | D | D | H | R
A2 | BASIC DESIGN DRAFT DOCUMENT LIST P&ID , LAY-OUT |  |  |  | H | H | R/A | R
A3 | KICK-OFF MEETING CUSTOMER DETAILLED DESIGN |  |  |  | D | H | H | H
A4 | PREPARE FINAL DESIGN |  |  |  | H | H | R/A | R
DOCUMENTS FOR APPROVAL
A5 | VENDOR DESIGN DOCUMENTS REVIEW |  |  |  | H | H | R/A | R | As per VPIS
B MATERIAL SELECTION / SUBCONTRACTOR ORDERING
B0 | GENERAL | ALL ITEMS SUITABLE FOR AMBIENT TEMPERATURE / OUTDOOR | MATERIAL SUPPLY |  | D | D | - | -
|  | ALL ITEMS TO BE CONFORM ZONE 2 GROUP IIB T3 | FABRICATION SCHEDULE
QA / QC
B1 | COMPRESSOR- MAYEKAWA (MYCOM) FACTORY | DETAILS AS PER COMPRESSOR QUALITY PLAN | TEST REPORT : - Noise test - Vibration test - Perfromance test - Running test - Hydro test | MATERIAL CERTIFICATES | D | D | R | R
MYCOM STANDARD Procedures
B2 | MAIN MOTOR | AS PER MANUFACTURER'S TEST PROCEDURES | TEST REPORT ( Manuf. Std ) |  | D | D | R | R
|  | HAZARDUS AREA CERTIFICATES | - Unwitenssed routine test report
B3 | OIL PUMP- MAYEKAWA FACTORY | MYCOM MANUFACTURER STANDARD Test Procedure | TEST REPORT incl; Hydro test result and performance test result | MATERIAL CERTIFICATES | D | R | R | R
B4 | OIL PUMP MOTOR | MANUFACTURER STANDARD | TEST REPORT ( Manuf. Std ) |  | D | R | R | R
|  | HAZARDOUS AREA CERTIFICATE | - Unwitenssed routine test report
B5 | MAIN COUPLING | API671 with Deviation (Flexible disc type coupling) | SUITABLE FOR HAZARDOUS AREA | MATERIAL CERTIFICATES | D | R | R | R
NOTE : CERTIFIED COMPLETE: ENDORSEMENTS:

## Table 2
|  | Gachsaran Polymer Industries Company HDPE Plant | [6 empty] | SHEET: 1 OF 5
DATE: 21.Jan.2025
P.O. No: GPIC-PT-MA-PO-000-3029 |  | Inspection And Test Plan (ITP) for Refrigerator Package | [6 empty] | REV.: 00
P.O. Title: Refrigeration Unit Package |  | VENDOR DOC. NO.: VD-GPIC-MA-3029-3029-0003 | [6 empty] | BY : MO
ITEM NO(S).: PK6101
1 | SCOPE | This Inspection and Test plan covers all activtiies that will be carrived out in design and farbrication of equipment.
2 | LEGEND OF THE TECHNICAL SURVEILLANCE | 1) (H)= INSPECTION NOTIFICATION will be issued by manufacturer and inspection shall be performed at presence of notified party. Next farbication stage is subject to acceptance of inspection. Vendor must notify parties (see inspection activtiy) of the defidcated inspection activity at least fifteen (15) days in advance.
2) (SW)=10% OF TYPE/LOT WITNESSED. Action performed only on a certain number of pieces.
3) (W)=WITNESSING. The Supplier shall inform the NOTIFIED PARTY of the date of the activity and the NOTIFIED PARTY reserves the right to witness the test. If the test is conducted at the notified date, the Supplier may proceed with the subsequent phase, even if the NOTIFIED did not witness the test.
4) (R/A)=REVIEW OF TECHNICAL DOCUMENTS BEFORE COMMENCEMENT OF CONSTRUCTION. The technical documents shall be reviewed and approved before the commencement of construction
5) (R )=REVIEW OF DOCUMENTS. Materials certificates, statement of compliance and reports of inspection and tests conducted by the Supplier shall be revised to assess their conformance with the requirements specified in the Code and Standards, Specifications and/or Purchase Order.
6) (D) = Vendor Inspection
3 | Abbreviations | O= Owner (GPIC) C= Contractor (EIED) V= Vendor (HSE/RHINE) SV = Sub Vendor TPI = Third Party Inspection on behalf of owner
Item No. | Inspection Description | References / Specifications / Codes | Verifying Document | Acceptance Criteria | INSPECTION ACTIVITY |  |  |  | REMARKS | R E V
[5 empty] | SUB-VENDOR (SV) | VENDOR (V) | EIED(C) | O/TPI
B MATERIAL SELECTION / SUBCONTRACTOR ORDERING (CONTINUE)
B6 | RECEIVER | ASME VIII DIV 1 (U-STAMP NOT REQUIRED ) (Welding_Standard) | 1) MATERIAL CERTIFICATES 3.1 FOR PRESSURE RETAINING PARTS 2.2 WELD FILLER AND NON PRESSURE RETAINING PARTS | VD-GPIC-MA-3029-3029-0024 | H | H | R | R
|  |  | WPS/PQR – WELDER QUALIFICATIONS WELDING CHECK NDE REPORTS CLEANLINESS TREATMENT RT REQUIREMENT FULL (on pressure retaining parts) PAINTING INSPECTION |  | H | H | R | R
|  |  | DIMENSIONAL CHECK |  | H | H | W | W
|  |  | HYDROSTATIC TEST |  | H | H | H | H
| OIL SEPARATOR (WITH COALESCERS) | ASME VIII DIV 1 (U-STAMP NOT REQUIRED) | 1) MATERIAL CERTIFICATES 3.1 FOR PRESSURE RETAINING PARTS 2.2 WELD FILLER AND NON PRESSURE RETAINING PARTS WPS/PQR – WELDER QUALIFICATIONS WELDING CHECK NDE REPORTS CLEANLINESS TREATMENT RT REQUIREMENT FULL (on pressure retaining parts) DIMENSIONAL CHECK HYDROSTATIC TEST PAINTING INSPECTION | VD-GPIC-MA-3029-3029-0024 | H | W | R | R
| OIL FILTER | ASME VIII DIV 1 (U-STAMP NOT REQUIRED) | 1) MATERIAL CERTIFICATES 3.1 FOR PRESSURE RETAINING PARTS NDE REPORTS CLEANLINESS TREATMENT INTERNAL INSPECTION (Visual Examination) VISUAL CHECK DIMENSIONAL CHECK HYDROSTATIC TEST PAINTING INSPECTION | VD-GPIC-MA-3029-3029-0024 | H | H | R | R
B7 | HEAT EXCHANGERS 1. CONDENSER 2. OIL COOLER 3. ECONOMIZER 4. CHILLER (EVAPORATOR) | ASME VIII DIV 1 (U-STAMP NOT REQUIRED) TEMA | MATERIAL CERTIFICATES 3.1 FOR PRESSURE RETAINING PARTS 2.2 WELD FILLER AND NON PRESSURE RETAINING PARTS | VD-GPIC-MA-3029-3029-0027 | H | W | R | R
|  |  | WPS/PQR – WELDER QUALIFICATIONS WELDING CHECK NDE REPORTS CLEANLINESS TREATMENT RT REQUIREMENT FULL (on pressure retaining parts) PAINTING INSPECTION |  | H | H | R | R
|  |  | DIMENSIONAL CHECK |  | H | H | W | W
|  |  | HYDROSTATIC TEST |  | H | H | H | H
B8 | BASE FRAME | MANUFACTURER STANDARD Design Suitable for This Series of Compressor | PT -10 % OF MAJOR STRUCTURAL CONNECTIONS 100 % PT LIFTING LUG WELDS 100 % RT BUTT WELDS IN MAJOR SUPPORTING BEAMS | ACC. Vendor DATASHEET/DRAWING SKID CONNECTION POINTS – ANCHOR BOLT POSITIONS INSPECTION /CERTIFICATE | D | R | R | R
B9 | VALVES | ASME/MFR STD For Special Valves | MATERIAL CERTIFICATES 3.1 FOR MAJOR PARTS HYDROSTATIC REPORT PAINTING INSPECTION | ACC. Vendor DATASHEET/DRAWING INSPECTION /CERTIFICATE | D | R | R | R
B10 | PIPING | ASTM | 1) CARBON OIL AND REFRIGERANT PIPING 10% . 2) SS Oil AND REFRIGERANT PIPING 10%. 3) INSTRUMENT AIR HEADER10% . AMOUNT WILL BE BASED ON TOTAL AMOUNT OF WELDED INCHES. | MATERIAL CERTIFICATES | D | R | R | R
B11 | SAFETY VALVES | ASME VIII DIV 1 without U-Stamp | MATERIAL CERTIFICATES 2.2 SET PRESSURE TEST REPORT CALCULATIONS TEST REPORT | INSPECTION CERTIFICATE | D | R | R | R
VD-GPIC-MA-3029-3029-0041
B12 | Smaller components within instrumenetation routing, such as TUBING AND GASKETS and bolting . |  | MATERIAL CERTIFICATES 3.1 | INSPECTION CERTIFICATE | D | R | R | R
B13 | INSTRUMENTATION | Pressure, Temperature and Level Guages and Transmiters are provided with 2.2 material certificates. | MATERIAL CERTIFICATES 2.2 HAZARDOUS AREA CERTIFICATE | INSPECTION CERTIFICATE VD-GPIC-MA-3029-3029-0038 | D | R | R | R
CALIBRATION REPORT
NOTE : CERTIFIED COMPLETE: ENDORSEMENTS:

## Table 3
|  | Gachsaran Polymer Industries Company HDPE Plant | [6 empty] | SHEET: 1 OF 5
DATE: 21.Jan.2025
P.O. No: GPIC-PT-MA-PO-000-3029 |  | Inspection And Test Plan (ITP) for Refrigerator Package | [6 empty] | REV.: 00
P.O. Title: Refrigeration Unit Package |  | VENDOR DOC. NO.: VD-GPIC-MA-3029-3029-0003 | [6 empty] | BY : MO
ITEM NO(S).: PK6101
1 | SCOPE | This Inspection and Test plan covers all activtiies that will be carrived out in design and farbrication of equipment.
2 | LEGEND OF THE TECHNICAL SURVEILLANCE | 1) (H)= INSPECTION NOTIFICATION will be issued by manufacturer and inspection shall be performed at presence of notified party. Next farbication stage is subject to acceptance of inspection. Vendor must notify parties (see inspection activtiy) of the defidcated inspection activity at least fifteen (15) days in advance.
2) (SW)=10% OF TYPE/LOT WITNESSED. Action performed only on a certain number of pieces.
3) (W)=WITNESSING. The Supplier shall inform the NOTIFIED PARTY of the date of the activity and the NOTIFIED PARTY reserves the right to witness the test. If the test is conducted at the notified date, the Supplier may proceed with the subsequent phase, even if the NOTIFIED did not witness the test.
4) (R/A)=REVIEW OF TECHNICAL DOCUMENTS BEFORE COMMENCEMENT OF CONSTRUCTION. The technical documents shall be reviewed and approved before the commencement of construction
5) (R )=REVIEW OF DOCUMENTS. Materials certificates, statement of compliance and reports of inspection and tests conducted by the Supplier shall be revised to assess their conformance with the requirements specified in the Code and Standards, Specifications and/or Purchase Order.
6) (D) = Vendor Inspection
3 | Abbreviations | O= Owner (GPIC) C= Contractor (EIED) V= Vendor (HSE/RHINE) SV = Sub Vendor TPI = Third Party Inspection on behalf of owner
Item No. | Inspection Description | References / Specifications / Codes | Verifying Document | Acceptance Criteria | INSPECTION ACTIVITY |  |  |  | REMARKS | R E V
[5 empty] | SUB-VENDOR (SV) | VENDOR (V) | EIED(C) | O/TPI
C SUBVENDOR INSPECTION DOCUMENTS, PIPING
C1 | WELDING DOCUMENTS (WPS/PQR/WELD MAP) | ASME VIII Div 1, ASME IX Not Applicable |  |  | R/A | R | - | -
C2 | WELDER'S QUALIFICATION | ASME IX | CERTIFICATES |  | R/A | R | R | R
C3 | NDE PROCEDURES (UT/RT/MT/PT/HT) | ASME V | NDT Map |  | R/A | R | R/A | R
1) Carbon oil and refrigerant piping 10% . 2) SS Oil and refrigerant piping 10%. 3) Instrument air header 10% . Amount will be based on total amount of welded inches.
C4 | NDT OPERATORS AND INTERPRETERS QUALIFICATION | ASME V | CERTIFICATES |  | R/A | R | R | R
C5 | LEAK TEST PROCEDURE (PNEUMATIC AND/OR HYDRAULIC) | ASME VIII DIV. 1 | MANUFACTURING STANDARD |  | R | R | R | R
C6 | MYCOM STANDARD / VENDOR PROCEDURES COATING PROCEDURE | MYCOM STANDARD / VENDOR PAINTING PROCEDURES |  | VD-GPIC-MA-3029-3029-0063 | R | R | R | R
C7 | RUST PRESERVATION PROCEDURE | MANUFACTURER STANDARD |  |  | R | R | R | R
NOTE : CERTIFIED COMPLETE: ENDORSEMENTS:

## Table 4
|  | Gachsaran Polymer Industries Company HDPE Plant | [6 empty] | SHEET: 1 OF 5
DATE: 21.Jan.2025
P.O. No: GPIC-PT-MA-PO-000-3029 |  | Inspection And Test Plan (ITP) for Refrigerator Package | [6 empty] | REV.: 00
P.O. Title: Refrigeration Unit Package |  | VENDOR DOC. NO.: VD-GPIC-MA-3029-3029-0003 | [6 empty] | BY : MO
ITEM NO(S).: PK6101
1 | SCOPE | This Inspection and Test plan covers all activtiies that will be carrived out in design and farbrication of equipment.
2 | LEGEND OF THE TECHNICAL SURVEILLANCE | 1) (H)= INSPECTION NOTIFICATION will be issued by manufacturer and inspection shall be performed at presence of notified party. Next farbication stage is subject to acceptance of inspection. Vendor must notify parties (see inspection activtiy) of the defidcated inspection activity at least fifteen (15) days in advance.
2) (SW)=10% OF TYPE/LOT WITNESSED. Action performed only on a certain number of pieces.
3) (W)=WITNESSING. The Supplier shall inform the NOTIFIED PARTY of the date of the activity and the NOTIFIED PARTY reserves the right to witness the test. If the test is conducted at the notified date, the Supplier may proceed with the subsequent phase, even if the NOTIFIED did not witness the test.
4) (R/A)=REVIEW OF TECHNICAL DOCUMENTS BEFORE COMMENCEMENT OF CONSTRUCTION. The technical documents shall be reviewed and approved before the commencement of construction
5) (R )=REVIEW OF DOCUMENTS. Materials certificates, statement of compliance and reports of inspection and tests conducted by the Supplier shall be revised to assess their conformance with the requirements specified in the Code and Standards, Specifications and/or Purchase Order.
6) (D) = Vendor Inspection
3 | Abbreviations | O= Owner (GPIC) C= Contractor (EIED) V= Vendor (HSE/RHINE) SV = Sub Vendor TPI = Third Party Inspection on behalf of owner
Item No. | Inspection Description | References / Specifications / Codes | Verifying Document | Acceptance Criteria | INSPECTION ACTIVITY |  |  |  | REMARKS | R E V
[5 empty] | SUB-VENDOR (SV) | VENDOR (V) | EIED(C) | O/TPI
D INSPECTION & TESTING DURING FABRICATION
D1 | ASSEMBLY START | INTERNAL PRODUCTION SCHEDULE / INSPECTION SCHEDULE | PT -10 % OF MAJOR STRUCTURAL CONNECTIONS 100 % PT LIFTING LUG WELDS 100 % RT BUTT WELDS IN MAJOR SUPPORTING BEAMS | VD-GPIC-MA-3029-3029-0075 | D | R | R | R
D2 | TRANSFER OF MATERIAL, IDENTIFICATION, MARKING & TRACEBILITY |  | WELDING AND MATERIAL TRACEABILITY LISTS | _ | D | R | R | R
D3 | PIPING | ASME V, ASME I X | WPS/PQR NDE REPORT | PIPING DESIGN CONFORMS TO ANSI B31.3 | D | R | R | R
See line seq. No C3
D4 | PNEUMATIC TEST PROCEDURE TO UNIT | NDE FOR PIPING SECTIONS ASME B31.3 DISMOUNTING OF SAFETY VALVES PRIOR START OF PNEUMATIC TEST | PNEUMATIC TEST PROCEDURE PNEUMATIC TEST REPORT | PNEUMATIC TESTING ON COMPLETE UNIT | D | W | SW | SW
E INSPECTION
E1 | DIMENSIONAL INSPECTION OF SKID CONNECTION POINTS |  | GENERAL ARRANGMENT DRAWING | VD-GPIC-MA-3029-3029-0062 | D | W | W | W
E2 | PARTS AND COMPONENT INSPECTION |  | P&ID | VD-GPIC-MA-3029-3029-0015 | D | W | W | W
NOTE : CERTIFIED COMPLETE: ENDORSEMENTS:

## Table 5
|  | Gachsaran Polymer Industries Company HDPE Plant | [6 empty] | SHEET: 1 OF 5
DATE: 21.Jan.2025
P.O. No: GPIC-PT-MA-PO-000-3029 |  | Inspection And Test Plan (ITP) for Refrigerator Package | [6 empty] | REV.: 00
P.O. Title: Refrigeration Unit Package |  | VENDOR DOC. NO.: VD-GPIC-MA-3029-3029-0003 | [6 empty] | BY : MO
ITEM NO(S).: PK6101
1 | SCOPE | This Inspection and Test plan covers all activtiies that will be carrived out in design and farbrication of equipment.
2 | LEGEND OF THE TECHNICAL SURVEILLANCE | 1) (H)= INSPECTION NOTIFICATION will be issued by manufacturer and inspection shall be performed at presence of notified party. Next farbication stage is subject to acceptance of inspection. Vendor must notify parties (see inspection activtiy) of the defidcated inspection activity at least fifteen (15) days in advance.
2) (SW)=10% OF TYPE/LOT WITNESSED. Action performed only on a certain number of pieces.
3) (W)=WITNESSING. The Supplier shall inform the NOTIFIED PARTY of the date of the activity and the NOTIFIED PARTY reserves the right to witness the test. If the test is conducted at the notified date, the Supplier may proceed with the subsequent phase, even if the NOTIFIED did not witness the test.
4) (R/A)=REVIEW OF TECHNICAL DOCUMENTS BEFORE COMMENCEMENT OF CONSTRUCTION. The technical documents shall be reviewed and approved before the commencement of construction
5) (R )=REVIEW OF DOCUMENTS. Materials certificates, statement of compliance and reports of inspection and tests conducted by the Supplier shall be revised to assess their conformance with the requirements specified in the Code and Standards, Specifications and/or Purchase Order.
6) (D) = Vendor Inspection
3 | Abbreviations | O= Owner (GPIC) C= Contractor (EIED) V= Vendor (HSE/RHINE) SV = Sub Vendor TPI = Third Party Inspection on behalf of owner
Item No. | Inspection Description | References / Specifications / Codes | Verifying Document | Acceptance Criteria | INSPECTION ACTIVITY |  |  |  | REMARKS | R E V
[5 empty] | SUB-VENDOR (SV) | VENDOR (V) | EIED(C) | O/TPI
E INSPECTION (CONTINUE)
E3 | PMI TEST (WELDS) | According to weld-NDT Map (If applicable) | INSPECTION CERTIFICATE | ASTM | D | W | SW | SW | Time period of PMI will be informed.No specific dates are consider to be informed in advance by Vendor
E4 | PAINTING | MYCOM STANDARD / VENDOR PAINTING PROCEDURE | THICKNESS VISUAL INSPECTION AND MEASUREMENT VIA INSTRUMENT. PAINT INSPECTION REPORT | VD-GPIC-MA-3029-3029-0063 | D | W | R | W
E5 | INSTRUMENT WIRING | MANUFACTURER STANDARD | Instrument, Junction Box and Local Control Panel location and Cable Routing Layout | VD-GPIC-MA-3029-3029-0047 | D | W | R | R
E6 | INSPECTION OF JUCTION BOX, LOCAL PANEL AND PLC | FACTORY ACCEPTANCE TEST FOR PLC 1) VISUAL INSPECTION JUNCTION BOX, LOCAL PANEL AND PLC 2) CONTINUITY, POWER UP & WET LOOP CHECK 3) FUNCTION TEST ( REDUNDANCY, LOGIC) | TEST REPORT FAT TEST PROCEDURE | VD-GPIC-MA-3029-3029-0037 | D | W | W | W
E7 | RUST PREVENTION FOR STORAGE | VENDOR STANDARD | NITROGEN CHARGING -0.5 BAR | VD-GPIC-MA-3029-3029-0007 | D | D | R | R
E8 | FINAL INSPECTION |  | NAME PLATES CONFIRMATION | RELEASE NOTE | D | H | H | H
E9 | APPROVAL OF CONCESSION REQUEST AND NON-CONFORMANCE REPORTS |  |  |  | D | R | R/A | R/A
F SHIPMENT AND LOADING
F1 | PACKING AND MARKING PREPARATION FOR SHIPMENT DETAILED PACKING LIST AND LOOSE DELIVERY LIST | PACKING INSPECTION | PACKING INSPECTION: VISUAL INSPECTION COMPLETENESS CHECK PACKING LIST | VD-GPIC-MA-3029-3029-0007 | D | H | R | R
F2 | DOCUMENTATION | AS PER APPROVED VPIS INCLUDING FINAL DATA BOOK, ITP, ETC. | A COMPLETE PACKAGE OF INSPECTION AND TEST RECORD/CERTIFICATE MANUFACTURED RECORD | VPIS & REPORTS | D | R/A | R/A | R/A
NOTE : CERTIFIED COMPLETE: ENDORSEMENTS: