## Cover Page
Gachsaran Polymer Industries Company HDPE Plant
Inspection And Test Plan (ITP) for Refrigerator Package
P.O. No: GPIC-PT-MA-PO-000-3029 |  |  | VENDOR DOC. NO.: VD-GPIC-MA-3029-3029-0003 |  |  | Rev. | Page 1 of 12
03
Inspection And Test Plan (ITP) for Refrigerator Package
|  | Code 1 | No Comment / Approved
(Applicable Only for “For Review” and "For Approval" Documents) No comment and the document are released for Manufacturing.
|  | Code 2 | No Comment/ Approved with Note(s)
Vendor/Sub- Contractor shall correct, revise and resubmit the document. The document is released for Manufacturing if changes incorporated.
|  | Code 3 | Commented
Vendor/Sub-Contractor shall correct, revise and resubmit the document by the date specified. The document shall be revised under the Status of “R: Revised Issue”. All corrected documents shall be resubmitted before starting the Manufacturing Process.
|  | Code 4 | Not Accepted ( Rejected )
Vendor/Sub-Contractor shall re-work / re-design / re-specify the contents of the document according to the comments / reasons for rejection. All corrected documents shall be resubmitted before starting the manufacturing. Vendor/Sub-Contractor shall not proceed with subsequent works of Material Supply or Manufacturing until receiving Code1/Code2 or No Code from PURCHASER. Vendor/Sub-Contractor shall resubmit the document with the same revision within 6 working days after receiving comments.
|  | No Code | No Code
(Only for “For Information” Documents and “As Built DWGs”) Document has been submitted for PURCHASER's Information (FI). Consistency, completeness and correctness of document content is in Vendor/Sub-Contractor's responsibility.
Date:
Dept.:
Signature:
Above checking results by EIED shall in no way relieve Vendor of any liability, obligation and responsibility out of the purchase order and the mutual agreement in writing.
| 03 | 05.08.2025 | IFA | N.B | F.T | A.M
| 02 | 16.07.2025 | IFA | A.M | F.T | A.M
| 01 | 27.05.2025 | IFA | A.M | F.T | A.M
| 00 | 21.04.2025 | IFA | N.B | F.T | A.M
| Rev. | Date (DD.MMM.YY) | Purpose OF Issue | Prepared | Checked | Approved
Note on C36: Date should be added in a long format

## Index
Gachsaran Polymer Industries Company HDPE Plant
Inspection And Test Plan (ITP) for Refrigerator Package
P.O. No: GPIC-PT-MA-PO-000-3029 |  |  | VENDOR DOC. NO.: VD-GPIC-MA-3029-3029-0003 | [6 empty] | Rev | Page 2 of 12
03
REVISION INDEX
| Rev. Page | 00 | 01 | 02 | 03 | 04 | Rev. Page | 00 | 01 | 02 | 03 | 04
| 1 | X | X | X | X |  | 34
| 2 | X | X | X | X |  | 35
| 3 | X | X | X | X |  | 36
| 4 | X | X | X | X |  | 37
| 5 | X | X | X | X |  | 38
| 6 | X | X | X | X |  | 39
| 7 | X | X | X | X |  | 40
| 8 | X | X | X | X |  | 41
| 9 |  |  | X | X |  | 42
| 10 |  |  | X | X |  | 43
| 11 |  |  | X | X |  | 44
| 12 |  |  | X | X |  | 45
| 13 | [5 empty] | 46
| 14 | [5 empty] | 47
| 15 | [5 empty] | 48
| 16 | [5 empty] | 49
| 17 | [5 empty] | 50
| 18 | [5 empty] | 51
| 19 | [5 empty] | 52
| 20 | [5 empty] | 53
| 21 | [5 empty] | 54
| 22 | [5 empty] | 55
| 23 | [5 empty] | 56
| 24 | [5 empty] | 57
| 25 | [5 empty] | 58
| 26 | [5 empty] | 59
| 27 | [5 empty] | 60
| 28 | [5 empty] | 61
| 29 | [5 empty] | 62
| 30 | [5 empty] | 63
| 31 | [5 empty] | 64
| 32 | [5 empty] | 65
| 33 | [5 empty] | 66

## Steps
|  | Gachsaran Polymer Industries Company HDPE Plant | Page : 03 Of 12
DATE: 05.08.2025
P.O. No: GPIC-PT-MA-PO-000-3029 |  | Inspection And Test Plan (ITP) for Refrigerator Package | REV.: 03
P.O.Title: Refrigeration Unit Package |  | VENDOR DOC. NO.: VD-GPIC-MA-3029-3029-0003 | BY : MO
ITEM NO(S).: PK6101
1 | SCOPE | This Inspection and Test plan covers all activtiies that will be carrived out in design and farbrication of equipment.
2 | LEGEND OF THE TECHNICAL SURVEILLANCE | 1) (H)= INSPECTION NOTIFICATION will be issued by manufacturer and inspection shall be performed at presence of notified party. Next farbication stage is subject to acceptance of inspection. Vendor must notify parties (see inspection activtiy) of the defidcated inspection activity at least fifteen (15) days in advance.
2) (SW)=10% OF TYPE/LOT WITNESSED. Action performed only on a certain number of pieces.
3) (W)=WITNESSING. The Supplier shall inform the NOTIFIED PARTY of the date of the activity and the NOTIFIED PARTY reserves the right to witness the test. If the test is conducted at the notified date, the Supplier may proceed with the subsequent phase, even if the NOTIFIED did not witness the test.
4) (R/A)=REVIEW OF TECHNICAL DOCUMENTS BEFORE COMMENCEMENT OF CONSTRUCTION. The technical documents shall be reviewed and approved before the commencement of construction
5) (R )=REVIEW OF DOCUMENTS. Materials certificates, statement of compliance and reports of inspection and tests conducted by the Supplier shall be revised to assess their conformance with the requirements specified in the Code and Standards, Specifications and/or Purchase Order.
6) (D) = Vendor Inspection
3 | Abbreviations | O/MC= Owner (PIDMCO) C= Contractor (EIED) V= Vendor (HSE/RHINE) SV = Sub Vendor TPI = Third Party Inspection on behalf of owner
Hold (H): Hold point is a designate point during or following specific activities which are defined in ITP and which inspection or examination shall not proceed unless the designate parties have witnessed the inspection or examination or test. TPA shall sign and stamp all related reports as HOLD POINT, and results all activates shall be specified clearly by term Accepted / Rejected. Vendor/Contractor shall be informed other party at least 7 working days prior to subject action. Witness (W): Witness point is a designate point during or following an important activity at which inspection or examination is required in according with the relative procedures. Work may proceed through the designate witness point if the inspector is not present for the previously established activity. TPA shall sign and stamp all related reports as “Witnessed by TPA” and results all activates shall be specified clearly by term Accepted / Rejected. Vendor/Contractor shall be informed other party at least 3 working days prior to subject action. Review(R): It is proceed though reviewing any result of inspection or test as a method of ensuring that the inspecting of test is performed in accordance with any approved procedure, specification or acceptance criteria. Inspection result shall review, but presence of involved party at inspection time is not mandatory, all documents shall be sign and stamp as reviewed and results all activates shall be specified clearly by term accepted / Rejected. Also, TPA shall be Reviewed document in 7 days. Review and Approved (RA): RA means that documents reviewed by involved party shall be signed and stamped as reviewed and approved. Where a document is subjected to party approval, work shall not proceed until related party approved is obtained. Spot witness (SW): Include a wide variety of action taken by charge person to inspect, check, control of activities and their sequence by means of observation, information collection, and verbal instruction of the activities; verify the routing and supporting documents for the purpose of proper expedition. Any non-conformity found during above mentioned inspection by TPA shall be reported to SUPPLIER and CONTRACTOR/PURCHASER and COMPANY immediately. Vendor shall send notification for SW point.
NOTE : CERTIFIED COMPLETE: ENDORSEMENTS:

## Table 1
|  | Gachsaran Polymer Industries Company HDPE Plant | [7 empty] | Page : 04 Of 12
DATE: 05.08.2025
P.O. No: GPIC-PT-MA-PO-000-3029 |  | Inspection And Test Plan (ITP) for Refrigerator Package | [7 empty] | REV.: 03
P.O.Title: Refrigeration Unit Package |  | VENDOR DOC. NO.: VD-GPIC-MA-3029-3029-0003 | [7 empty] | BY : MO
ITEM NO(S).: PK6101
1 | SCOPE | This Inspection and Test plan covers all activtiies that will be carrived out in design and farbrication of equipment.
2 | LEGEND OF THE TECHNICAL SURVEILLANCE | 1) (H)= INSPECTION NOTIFICATION will be issued by manufacturer and inspection shall be performed at presence of notified party. Next farbication stage is subject to acceptance of inspection. Vendor must notify parties (see inspection activtiy) of the defidcated inspection activity at least fifteen (15) days in advance.
2) (SW)=10% OF TYPE/LOT WITNESSED. Action performed only on a certain number of pieces.
3) (W)=WITNESSING. The Supplier shall inform the NOTIFIED PARTY of the date of the activity and the NOTIFIED PARTY reserves the right to witness the test. If the test is conducted at the notified date, the Supplier may proceed with the subsequent phase, even if the NOTIFIED did not witness the test.
4) (R/A)=REVIEW OF TECHNICAL DOCUMENTS BEFORE COMMENCEMENT OF CONSTRUCTION. The technical documents shall be reviewed and approved before the commencement of construction
5) (R )=REVIEW OF DOCUMENTS. Materials certificates, statement of compliance and reports of inspection and tests conducted by the Supplier shall be revised to assess their conformance with the requirements specified in the Code and Standards, Specifications and/or Purchase Order.
6) (D) = Vendor Inspection
3 | Abbreviations | O/MC= Owner (PIDMCO) C= Contractor (EIED) V= Vendor (HSE/RHINE) SV = Sub Vendor TPI = Third Party Inspection on behalf of owner
Item No. | Inspection Description | References / Specifications / Codes | Acceptance Criteria | Verifying Document | INSPECTION ACTIVITY |  |  |  |  | REMARKS | REV
[5 empty] | SUB-VENDOR (SV) | VENDOR (V) | EIED (C) | TPI | OWNER/ MC
A PROJECT PREPARATION
A1 | DOCUMENT REVIEW ACCORDING TO APPROVED VPIS | PROJECT DOCUMENTS AS PER VPIS | _ | _ | H | H | R | _ | R
A2 | PRE INSPECTION MEETING | INSPECTION AND TEST PLAN (ITP) | _ | ITP & PIM AGENDA | H | H | H | _ | H
B MATERIAL SELECTION / SUBCONTRACTOR ORDERING
B0 | GENERAL | ALL ITEMS SUITABLE FOR AMBIENT TEMPERATURE / OUTDOOR |  | MATERIAL SUPPLY | H | H | R | R | R
|  | ALL ITEMS TO BE CONFORM ZONE 2 GROUP IIB T3 |  | FABRICATION SCHEDULE
QA / QC
B1 | COMPRESSOR- MAYEKAWA (MYCOM) FACTORY | DETAILS AS PER COMPRESSOR QUALITY PLAN | MATERIAL CERTIFICATES | TEST REPORT : - Noise test - Vibration test - Perfromance test - Running test - Hydro test | H | H | R | R | R
MYCOM STANDARD Procedures
B2 | MAIN MOTOR | AS PER MANUFACTURER'S TEST PROCEDURES |  | TEST REPORT ( Manuf. Std ) | H | H | R | R | R
|  | HAZARDUS AREA CERTIFICATES |  | - Unwitenssed routine test report
B3 | OIL PUMP- MAYEKAWA FACTORY | MYCOM MANUFACTURER STANDARD Test Procedure | MATERIAL CERTIFICATES | TEST REPORT incl; Hydro test result and performance test result | H | H | R | R | R
B4 | OIL PUMP MOTOR | MANUFACTURER STANDARD |  | TEST REPORT ( Manuf. Std ) | H | H | R | R | R
|  | HAZARDOUS AREA CERTIFICATE |  | - Unwitenssed routine test report
B5 | MAIN COUPLING | API671 WITH DEVIATION (FLEXIBLE DISC TYPE COUPLING) | MATERIAL CERTIFICATES | SUITABLE FOR HAZARDOUS AREA | H | H | R | R | R
NOTE : CERTIFIED COMPLETE: ENDORSEMENTS:

## Table 2
|  | Gachsaran Polymer Industries Company HDPE Plant | [7 empty] | Page : 05 Of
DATE: 05.08.2025
P.O. No: GPIC-PT-MA-PO-000-3029 |  | Inspection And Test Plan (ITP) for Refrigerator Package | [7 empty] | REV.: 03
P.O. Title:Refrigeration Unit Package |  | VENDOR DOC. NO.: VD-GPIC-MA-3029-3029-0003 | [7 empty] | BY : MO
ITEM NO(S).: PK6101 | [11 empty] | Page 1 of 12
1 | SCOPE | This Inspection and Test plan covers all activtiies that will be carrived out in design and farbrication of equipment.
2 | LEGEND OF THE TECHNICAL SURVEILLANCE | 1) (H)= INSPECTION NOTIFICATION will be issued by manufacturer and inspection shall be performed at presence of notified party. Next farbication stage is subject to acceptance of inspection. Vendor must notify parties (see inspection activtiy) of the defidcated inspection activity at least fifteen (15) days in advance.
2) (SW)=10% OF TYPE/LOT WITNESSED. Action performed only on a certain number of pieces.
3) (W)=WITNESSING. The Supplier shall inform the NOTIFIED PARTY of the date of the activity and the NOTIFIED PARTY reserves the right to witness the test. If the test is conducted at the notified date, the Supplier may proceed with the subsequent phase, even if the NOTIFIED did not witness the test.
4) (R/A)=REVIEW OF TECHNICAL DOCUMENTS BEFORE COMMENCEMENT OF CONSTRUCTION. The technical documents shall be reviewed and approved before the commencement of construction
5) (R )=REVIEW OF DOCUMENTS. Materials certificates, statement of compliance and reports of inspection and tests conducted by the Supplier shall be revised to assess their conformance with the requirements specified in the Code and Standards, Specifications and/or Purchase Order.
6) (D) = Vendor Inspection
3 | Abbreviations | O/MC= Owner (PIDMCO) C= Contractor (EIED) V= Vendor (HSE/RHINE) SV = Sub Vendor TPI = Third Party Inspection on behalf of owner
Item No. | Inspection Description | References / Specifications / Codes | Acceptance Criteria | Verifying Document | INSPECTION ACTIVITY |  |  |  |  | REMARKS | REV
[5 empty] | SUB-VENDOR (SV) | VENDOR (V) | EIED (C) | TPI | OWNER/MC
B MATERIAL SELECTION / SUBCONTRACTOR ORDERING (CONTINUE)
B6 | RECEIVER | ASME VIII DIV 1 (U-STAMP NOT REQUIRED ) (Welding_Standard) | VD-GPIC-MA-3029-3029-0024 | 1) MATERIAL CERTIFICATES 3.1 FOR PRESSURE RETAINING PARTS 2.2 WELD FILLER AND NON PRESSURE RETAINING PARTS | H | H | W | W | R
|  |  |  | WPS/PQR – WELDER QUALIFICATIONS WELDING CHECK NDE REPORTS CLEANLINESS TREATMENT RT REQUIREMENT AS PER NDT MAP (on pressure retaining parts) PWHT (If Applicable) PAINTING INSPECTION | H | H | R | R | R
|  |  |  | DIMENSIONAL CHECK | H | H | W | W | R
|  |  |  | HYDROSTATIC TEST | H | H | W | W | R
B7 | OIL SEPARATOR (WITH COALESCERS) | ASME VIII DIV 1 (U-STAMP NOT REQUIRED) | VD-GPIC-MA-3029-3029-0024 | 1) MATERIAL CERTIFICATES 3.1 FOR PRESSURE RETAINING PARTS 2.2 WELD FILLER AND NON PRESSURE RETAINING PARTS WPS/PQR – WELDER QUALIFICATIONS WELDING CHECK NDE REPORTS CLEANLINESS TREATMENT RT REQUIREMENT AS PER NDT MAP (on pressure retaining parts) PWHT (If Applicable) DIMENSIONAL CHECK HYDROSTATIC TEST PAINTING INSPECTION | H | W | R | R | R | Material Certificate, Dimensional Check, Hydrostatic Test, Painting (Witness for EIED and TPI)
B8 | OIL FILTER | ASME VIII DIV 1 (U-STAMP NOT REQUIRED) | VD-GPIC-MA-3029-3029-0024 | 1) MATERIAL CERTIFICATES 3.1 FOR PRESSURE RETAINING PARTS NDE REPORTS CLEANLINESS TREATMENT INTERNAL INSPECTION (Visual Examination) VISUAL CHECK DIMENSIONAL CHECK HYDROSTATIC TEST PAINTING INSPECTION | H | H | R | R | R
B9 | HEAT EXCHANGERS 1. CONDENSER 2. OIL COOLER 3. ECONOMIZER 4. CHILLER (EVAPORATOR) | ASME VIII DIV 1 (U-STAMP NOT REQUIRED) TEMA | VD-GPIC-MA-3029-3029-0027 | MATERIAL CERTIFICATES 3.1 FOR PRESSURE RETAINING PARTS 2.2 WELD FILLER AND NON PRESSURE RETAINING PARTS | H | W | W | W | R
|  |  |  | WPS/PQR – WELDER QUALIFICATIONS WELDING CHECK NDE REPORTS CLEANLINESS TREATMENT RT REQUIREMENT AS PER NDT MAP (on pressure retaining parts) PWHT (If Applicable) PAINTING INSPECTION | H | H | R | R | R
|  |  |  | DIMENSIONAL CHECK | H | H | W | W | R
|  |  |  | HYDROSTATIC TEST | H | H | W | W | R
B10 | BASE FRAME | MANUFACTURER STANDARD Design Suitable for This Series of Compressor | ACC. Vendor DATASHEET/DRAWING SKID CONNECTION POINTS – ANCHOR BOLT POSITIONS INSPECTION /CERTIFICATE | PT -10 % OF MAJOR STRUCTURAL CONNECTIONS 100 % PT LIFTING LUG WELDS 100 % RT BUTT WELDS FOR SUPPORTING BEAMS (IF APPLICABLE) | D | R | R | R | R | DIMENSIONAL CHECK (Witness BY EIED &TPI)
B11 | VALVES | ASME/MFR STD For Special Valves | ACC. Vendor DATASHEET/DRAWING INSPECTION /CERTIFICATE | MATERIAL CERTIFICATES 3.1 FOR MAJOR PARTS HYDROSTATIC REPORT PAINTING INSPECTION | D | R | R | R | R
B12 | SAFETY VALVES | ASME VIII DIV 1 without U-Stamp | INSPECTION CERTIFICATE | MATERIAL CERTIFICATES 2.2 SET PRESSURE TEST REPORT CALCULATIONS TEST REPORT | D | R | R | R | R
B13 | Smaller components within instrumenetation routing, such as TUBING AND GASKETS and bolting . | ASTM STANDARD | INSPECTION CERTIFICATE | MATERIAL CERTIFICATES 3.1 | D | R | R | R | R
B14 | INSTRUMENTATION | Pressure, Temperature and Level Guages and Transmiters are provided with 2.2 material certificates. | INSPECTION CERTIFICATE INSTRUMENT DATA SHEET | MATERIAL CERTIFICATES 2.2 HAZARDOUS AREA CERTIFICATE | D | R | R | R | R
CALIBRATION REPORT
NOTE : CERTIFIED COMPLETE: ENDORSEMENTS:

## Table 3
|  | Gachsaran Polymer Industries Company HDPE Plant | [7 empty] | Page : 09 Of
DATE: 05.08.2025
P.O. No: GPIC-PT-MA-PO-000-3029 |  | Inspection And Test Plan (ITP) for Refrigerator Package | [7 empty] | REV.: 03
P.O. Title:Refrigeration Unit Package |  | VENDOR DOC. NO.: VD-GPIC-MA-3029-3029-0003 | [7 empty] | BY : MO
ITEM NO(S).: PK6101 | [11 empty] | Page 1 of 12
1 | SCOPE | This Inspection and Test plan covers all activtiies that will be carrived out in design and farbrication of equipment.
2 | LEGEND OF THE TECHNICAL SURVEILLANCE | 1) (H)= INSPECTION NOTIFICATION will be issued by manufacturer and inspection shall be performed at presence of notified party. Next farbication stage is subject to acceptance of inspection. Vendor must notify parties (see inspection activtiy) of the defidcated inspection activity at least fifteen (15) days in advance.
2) (SW)=10% OF TYPE/LOT WITNESSED. Action performed only on a certain number of pieces.
3) (W)=WITNESSING. The Supplier shall inform the NOTIFIED PARTY of the date of the activity and the NOTIFIED PARTY reserves the right to witness the test. If the test is conducted at the notified date, the Supplier may proceed with the subsequent phase, even if the NOTIFIED did not witness the test.
4) (R/A)=REVIEW OF TECHNICAL DOCUMENTS BEFORE COMMENCEMENT OF CONSTRUCTION. The technical documents shall be reviewed and approved before the commencement of construction
5) (R )=REVIEW OF DOCUMENTS. Materials certificates, statement of compliance and reports of inspection and tests conducted by the Supplier shall be revised to assess their conformance with the requirements specified in the Code and Standards, Specifications and/or Purchase Order.
6) (D) = Vendor Inspection
3 | Abbreviations | O/MC= Owner (PIDMCO) C= Contractor (EIED) V= Vendor (HSE/RHINE) SV = Sub Vendor TPI = Third Party Inspection on behalf of owner
Item No. | Inspection Description | References / Specifications / Codes | Acceptance Criteria | Verifying Document | INSPECTION ACTIVITY |  |  |  |  | REMARKS | REV
[5 empty] | SUB-VENDOR (SV) | VENDOR (V) | EIED (C) | TPI | OWNER/MC
C SUBVENDOR INSPECTION DOCUMENTS, PIPING
C1 | PIPING MATERIAL | ASTM STANDARD | MATERIAL CERTIFICATE | MATERIAL CERTIFICATE OR SAMPLING FOR TEST | H | H | W | W | R
C2 | WELDING DOCUMENTS (WPS/PQR/WELD MAP) | ASME B31.3, ASME IX | WPS/PQR/WELD MAP | PQR LAB RESULTS | R/A | R | R | R | R
C3 | WELDER'S QUALIFICATION | ASME IX | ASME IX | CERTIFICATES | R/A | R | R | R | R
C4 | NDE (UT/RT/MT/PT/HT) | ASME V | NDT PROCEDURE/NDT MAP | NDT REPORT | R/A | R | R/A | R | R
1) Carbon oil and refrigerant piping. 2) SS Oil and refrigerant piping. 3) Instrument air header. Amount will be based on total amount of welded inches.
C5 | NDT OPERATORS AND INTERPRETERS QUALIFICATION | ASME V | NDT PROCEDURE | CERTIFICATES | R/A | R | R | R | R
C6 | LEAK TEST (PNEUMATIC AND/OR HYDRAULIC) | ASME B31.3 | TEST PROCEDURE | TEST REPORT | H | H | W | W | R
C7 | PAINTING/ COATING | PAINTING PROCEDURE | PAINTING PROCEDURE | TEST REPORT | H | H | W | W | R
NOTE : CERTIFIED COMPLETE: ENDORSEMENTS:

## Table 4
|  | Gachsaran Polymer Industries Company HDPE Plant | [7 empty] | Page : 10 Of
DATE: 05.08.2025
P.O. No: GPIC-PT-MA-PO-000-3029 |  | Inspection And Test Plan (ITP) for Refrigerator Package | [7 empty] | REV.: 03
P.O. Title: Refrigeration Unit Package |  | VENDOR DOC. NO.: VD-GPIC-MA-3029-3029-0003 | [7 empty] | BY : MO
ITEM NO(S).: PK6101
1 | SCOPE | This Inspection and Test plan covers all activtiies that will be carrived out in design and farbrication of equipment.
2 | LEGEND OF THE TECHNICAL SURVEILLANCE | 1) (H)= INSPECTION NOTIFICATION will be issued by manufacturer and inspection shall be performed at presence of notified party. Next farbication stage is subject to acceptance of inspection. Vendor must notify parties (see inspection activtiy) of the defidcated inspection activity at least fifteen (15) days in advance.
2) (SW)=10% OF TYPE/LOT WITNESSED. Action performed only on a certain number of pieces.
3) (W)=WITNESSING. The Supplier shall inform the NOTIFIED PARTY of the date of the activity and the NOTIFIED PARTY reserves the right to witness the test. If the test is conducted at the notified date, the Supplier may proceed with the subsequent phase, even if the NOTIFIED did not witness the test.
4) (R/A)=REVIEW OF TECHNICAL DOCUMENTS BEFORE COMMENCEMENT OF CONSTRUCTION. The technical documents shall be reviewed and approved before the commencement of construction
5) (R )=REVIEW OF DOCUMENTS. Materials certificates, statement of compliance and reports of inspection and tests conducted by the Supplier shall be revised to assess their conformance with the requirements specified in the Code and Standards, Specifications and/or Purchase Order.
6) (D) = Vendor Inspection
3 | Abbreviations | O/MC= Owner (PIDMCO) C= Contractor (EIED) V= Vendor (HSE/RHINE) SV = Sub Vendor TPI = Third Party Inspection on behalf of owner
Item No. | Inspection Description | References / Specifications / Codes | Acceptance Criteria | Verifying Document | INSPECTION ACTIVITY |  |  |  |  | REMARKS | REV
[5 empty] | SUB-VENDOR (SV) | VENDOR (V) | EIED (C) | TPI | OWNER/MC
D INSPECTION
D1 | DIMENSIONAL INSPECTION OF SKID CONNECTION POINTS | GENERAL ARRANGMENT DRAWING | APPROVED GAD | REPORT | H | H | W | W | R
D2 | PARTS AND COMPONENT INSPECTION | PIPING AND INSTRUMENTATION DIAGRAM | APPROVED P&ID | REPORT | H | H | W | W | R
D3 | PNEUMATIC TEST OF UNITS | HYDROSTATIC TEST PROCEDURE | APPROVED HYDROSTATIC TEST PROCEDURE | REPORT | H | H | W | W | SW
NOTE : CERTIFIED COMPLETE: ENDORSEMENTS:

## Table 5
|  | Gachsaran Polymer Industries Company HDPE Plant | [7 empty] | Page : 11 Of
DATE: 05.08.2025
P.O. No: GPIC-PT-MA-PO-000-3029 |  | Inspection And Test Plan (ITP) for Refrigerator Package | [7 empty] | REV.: 03
P.O. Title: Refrigeration Unit Package |  | VENDOR DOC. NO.: VD-GPIC-MA-3029-3029-0003-02 | [7 empty] | BY : MO
ITEM NO(S).: PK6101
1 | SCOPE | This Inspection and Test plan covers all activtiies that will be carrived out in design and farbrication of equipment.
2 | LEGEND OF THE TECHNICAL SURVEILLANCE | 1) (H)= INSPECTION NOTIFICATION will be issued by manufacturer and inspection shall be performed at presence of notified party. Next farbication stage is subject to acceptance of inspection. Vendor must notify parties (see inspection activtiy) of the defidcated inspection activity at least fifteen (15) days in advance.
2) (SW)=10% OF TYPE/LOT WITNESSED. Action performed only on a certain number of pieces.
3) (W)=WITNESSING. The Supplier shall inform the NOTIFIED PARTY of the date of the activity and the NOTIFIED PARTY reserves the right to witness the test. If the test is conducted at the notified date, the Supplier may proceed with the subsequent phase, even if the NOTIFIED did not witness the test.
4) (R/A)=REVIEW OF TECHNICAL DOCUMENTS BEFORE COMMENCEMENT OF CONSTRUCTION. The technical documents shall be reviewed and approved before the commencement of construction
5) (R )=REVIEW OF DOCUMENTS. Materials certificates, statement of compliance and reports of inspection and tests conducted by the Supplier shall be revised to assess their conformance with the requirements specified in the Code and Standards, Specifications and/or Purchase Order.
6) (D) = Vendor Inspection
3 | Abbreviations | O/MC= Owner (PIDMCO) C= Contractor (EIED) V= Vendor (HSE/RHINE) SV = Sub Vendor TPI = Third Party Inspection on behalf of owner
Item No. | Inspection Description | References / Specifications / Codes | Acceptance Criteria | Verifying Document | INSPECTION ACTIVITY |  |  |  |  | REMARKS | REV
[5 empty] | SUB-VENDOR (SV) | VENDOR (V) | EIED (C) | TPI | OWNER/MC
D INSPECTION (CONTINUE)
D4 | PAINTING | MYCOM STANDARD / VENDOR PAINTING PROCEDURE / PAINTING PROCEDURE AS PER VPIS | APPROVED PAINTING PROCEDURE | REPORT | H | H | W | W | R
D5 | INSTRUMENT WIRING | MANUFACTURER STANDARD | APPROVED INSTRUMENT, JUNCTION BOX, AND LOCAL CONTROL PANEL LOCATION AND CABLE ROUTING LAYOUT | REPORT | H | H | W | W | R
D6 | INSPECTION OF JUCTION BOX, LOCAL PANEL | VISUAL INSPECTION JUNCTION BOX, LOCAL PANEL | APPROVED LCP AND JUNCTION BOX LAYOUT, ARRANGMENT AND WIRING DRAWING | REPORT | H | H | W | W | R
D7 | INSPECTION OF UCP | FUNCTION TEST OF UCP | APPROVED FAT PROCEDURE FOR UCP | REPORT | H | H | W | W | R
E SHIPMENT AND LOADING
E1 | PACKING AND MARKING INSPECTION | PACKING PROCEDURE | APPROVED Marking & Packing Procedure | PACKING LIST | H | H | H | H | R
E2 | INSPECTION RELEASE NOTE |  | INSPETION RELEASE NOTE | INSPECTION RELEASE NOTE | _ | _ | R | H | R
E3 | FINAL DATA BOOK | FINAL DATA BOOK INDEX | VPIS & REPORTS | FINAL DATA BOOK | _ | H | R | R | _
NOTE : CERTIFIED COMPLETE: ENDORSEMENTS: