## Resolution Sheet
|  |  |  | PROJECT: | Integrated Methanol and Ammonia Plant
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | IO list | N-278-VD-6019-IN-LIS-0006-01 (17735-06)
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 | Page 3 | 02 |  | Pressure transmitter second stage suction set points discrepancy with P&ID. | Noted. It will be updated according to per latest P&ID | Noted.
2 | Page 3 | 02 |  | Redundancy column should be added. | Since we're not providing the PLC, so we only mention the signals, but it is not our scope to implement redundancy. | Considering that the design and preparation of package documents is the responsibility of the vendor, to specify the type of signals in terms of redundancy , IS/NIS , Dry/Wet, 2wire/3wire according to the project specifications is the responsibility of the vendor too.
3 | Page 3 | 02 |  | All signals that cause trip status shoudl be considered redundant. | Since we're not providing the PLC, so we only mention the signals, but it is not our scope to implement redundancy. | Refer to item 2 reply.
4 | Page 3 | 02 |  | NIS | Noted. It will be incorporated. | Noted.
5 | Page 3 | 02 |  | 300LP-820 | Noted. It will be incorporated. | Noted.
Open
Closed