## Resolution Sheet
|  |  |  | PROJECT: | Integrated Methanol and Ammonia Plant
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | IO list | N-278-VD-6019-IN-LIS-0006-01 (17735-06)
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 | Page 3 | 02 |  | Pressure transmitter second stage suction set points discrepancy with P&ID. | Noted. It will be updated according to per latest P&ID | Noted.
2 | Page 3 | 02 |  | Redundancy column should be added. | Since we're not providing the PLC, so we only mention the signals, but it is not our scope to implement redundancy. | Considering that the design and preparation of package documents is the responsibility of the vendor, to specify the type of signals in terms of redundancy , IS/NIS , Dry/Wet, 2wire/3wire according to the project specifications is the responsibility of the vendor too. | Redundancy signals will be specified. Since Airpack is not providing PLC, redundant I/O channel is not Airpack's scope to implement.
3 | Page 3 | 02 |  | All signals that cause trip status shoudl be considered redundant. | Since we're not providing the PLC, so we only mention the signals, but it is not our scope to implement redundancy. | Refer to item 2 reply.
4 | Page 3 | 02 |  | NIS | Noted. It will be incorporated. | Noted.
5 | Page 3 | 02 |  | 300LP-820 | Noted. It will be incorporated. | Noted.
6 | Page 3 | 03 |  | Redundancy column should be added | Redundancy signals will be specified. Since Airpack is not providing PLC, redundant I/O channel is not Airpack's scope to implement. | Design and preparation of documents is vendor's scope.
7 | Page 3 | 03 |  | Re-Comment: refer to reply sheet All signals that cause trip Status should be considered redundant | Redundancy signals will be specified. Since Airpack is not providing PLC, redundant I/O channel is not Airpack's scope to implement. | Design and preparation of documents is vendor's scope. |  |  | Open
8 | Page 3 | 03 |  | As per latest VPIS, "01" is removed from all document No. | Noted. P&ID number will be updated. | Noted. |  |  | Closed
9 | Page 3 | 03 |  | As per TCL, Lamp test push button should be considered in LPS, then should be added in IO List and other related document. | Please recheck this item. According to PO, TCL and multiple revision documents this is not included. Also in the meeting at 2/1/2024 the layout is confirmed and closed. In order to close the P&ID the complete panel layout is discussed and confirmed to details as the colour of the light. Please let us know if you want an extra price for the pushbutton to implement this. | Noted.
10 | Page 3 | 03 |  | 320HS-8205 | Please refer to above item 9 | Noted.