## Resolution Sheet
|  |  |  | PROJECT: | Integrated Methanol and Ammonia Plant
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Main motor datasheet | N-278-VD-6019-PM-DS-0010-01 (17735-10)
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 |  | 2 | Closed | 0-49 DEG | Updated | closed
2 |  | 2 | Closed | 85% | This is the ambient design temperature from the order. So its kept 65 / 100 | closed
3 |  | 2 | Closed | 40+/-5% | Assumed 400V is meant by this comment. Updated | closed
4 |  | 2 | Closed | 50+/-2% | Updated | closed
5 |  | 2 | Closed | ?The motor is 3 phase | Updated | closed
6 |  | 2 | Closed | Power factor and efficiency shall be mentioned for 100, 75, 50 and 25% load | Added. | closed
7 |  | 3 | Closed | Attached project datasheet shall be filled. | This project template is not shared or included in the order. Therefor the Airpack standard template is used. | it was part of MR and shall be filled alomg with vendor motor data sheet. Please check attacched file. |  |  | Open
8 | [8 empty] | Closed
9
10
11
12
13
14
15
16
17
18
19
20