## Resolution Sheet
|  |  |  | PROJECT: | Integrated Methanol and Ammonia Plant
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Main motor datasheet | N-278-VD-6019-PM-DS-0010-01 (17735-10)
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 |  | 2 | Closed | 0-49 DEG | Updated
2 |  | 2 | Closed | 85% | This is the ambient design temperature from the order. So its kept 65 / 100
3 |  | 2 | Closed | 40+/-5% | Assumed 400V is meant by this comment. Updated
4 |  | 2 | Closed | 50+/-2% | Updated
5 |  | 2 | Closed | ?The motor is 3 phase | Updated
6 |  | 2 | Closed | Power factor and efficiency shall be mentioned for 100, 75, 50 and 25% load | Added.
7 |  | 3 | Closed | Attached project datasheet shall be filled. | This project template is not shared or included in the order. Therefor the Airpack standard template is used. | See below comment |  |  | Open
8 |  | 4 | Open | Project template as per attached file to be filled. | Native format is not shared at the beginning of the project. In the introduction email from our document controller and the project department it is clearly mentioned. |  |  |  | Closed
9
10
11
12
13
14
15
16
17
18
19
20