## Resolution Sheet
PROJECT:
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Instrument datasheets | 17735-12
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 | Page 1 | 01 | Closed | Any changes in next revision to be marked with revision mark. | Noted, changes will be marked with yellow background.
2 | Page 1 | 01 | Closed | If any comments is not applicable please send reply sheet. | Noted.
3 | Page 1 | 01 | Closed | Compatibility with project requirement is vendor responsibility and scope, and next comments are just for hint. | Noted.
4 | Page 1 | 01 | Closed | Compatibility with other vendor documents including PID,Hook-up, data sheet, and purchased instrument is vendor responsibility and scope. | Noted.
5 | Page 1 | 01 | Closed | Tag plate supply is scope of vendor and should added to data sheet as one of items. | Added to datasheet.
6 | Page 1 | 01 | Open | All Tag name in all document should be same format. no needs - after prefix 320. example correct format is 320PT-8201, 320TG-8204, ... | Please comment this on the P&ID.
7 | Page 1 | 01 | Open | For all instrument and accessories(Manifold), catalogue(including order code) should be submitted | It's ordered with the approved vendor list, but we cannot disclose this information |  |  |  | Open
8 | Page 3 | 01 | Closed | All - should be deleted in all of Tags. | See comment no. 6 |  |  |  | Closed
9 | Page 4 | 01 | Closed | Line Number should be added | Modified as requested.
10 | Page 4 | 01 | Closed | Area Classification should be added | Modified as requested.
11 | Page 4 | 01 | Closed | P&ID No. : N278-VD-6019-PR-PID-0002 | Modified as requested.
12 | Page 4 | 01 | Closed | Design temp 65°C -> 75°C | Noted.
13 | Page 4 | 01 | Closed | Should be Solid Front (For all PG) | Noted. It is already mentioned in the datasheet as blow-out protection. (line 25)
14 | Page 4 | 01 | Closed | Clarify "panel mounted with flange" | This means it will be put on a panel, and a flange is used for mounting it.
15 | Page 4 | 01 | Closed | Block valve(hand ball valve): plz clarify, sub vendor scope of supply or by Airpack | They are ordered separately by Airpack.
16 | Page 4 | 01 | Open | Manufacturer/model: Should be finalized and specified (For all PG) and relevant catalogs and order code should be submitted. | The datasheet will be updated after the instrument was ordered to have this information.
17 | Page 4 | 01 | Closed | Notes: The manifold material should be 316 Stainless Steel 2-valve complete of oval flanges with mounting bolts, gasket, etc | Noted.
18 | Page 5 | 01 | Closed | Norm. Pressure: 22.1 bar (g) Norm. Temperature: 60 °C PG-8202 is installed at the downstream of intercooler Design press.: 30.5 bar (g) [based on P&ID] Design temp.: 157°C | Modified to the correct values.
19 | Page 6 | 01 | Closed | Temperature norm./max.: plz recheck and modify / to be revised | Modified to the correct values.
20 | Page 7 | 01 | Open | Design press.: 7 barg Design temp.: 75°C | The original values are correct according to the P&ID.
21 | Page 7 | 01 | Closed | Fluid state: vapor <- recheck and modified | Modified.
22 | Page 8 | 01 | Closed | Line Number should be added | Noted.
23 | Page 8 | 01 | Closed | Area Classification should be added | Noted.
24 | Page 8 | 01 | Closed | P&ID No. : N278-VD-6019-PR-PID-0002 | Noted
25 | Page 8 | 01 | Closed | Setpoint LL 7,5 bar(g) | Modified.
26 | Page 8 | 01 | Closed | Design temp 65°C -> 75°C | Modified.
27 | Page 8 | 01 | Open | Adjustable range: to be filled based on selected model | The datasheet will be updated with this information when available.
28 | Page 8 | 01 | Open | Area classification -> Enclosure class | Already in line 5 (ingress protection). Is this sufficient?
29 | Page 8 | 01 | Open | Add line for "Mounting" | There is already one on line 40
30 | Page 8 | 01 | Open | Over voltage or lightning protection should be considered. | Is there no surge protection in the 24VDC supply already?
31 | Page 8 | 01 | Closed | Block valve(hand ball valve): no <- incompatible with PID document, plz clarify | Corrected to reflect P&ID
32 | Page 8 | 01 | Open | Mounting facilities: Bracket/ Suitable for 2" pipe,316SST | The mounting is not yet finalized. Usually the PT is not mounted on the pipe.
33 | Page 8 | 01 | Open | Manufacturer/model: Should be finalized and specified (For all PT) and relevant catalogs and order code should be submitted. | see comment no. 16
34 | Page 8 | 01 | Closed | The manifold material should be 316 Stainless Steel 2-valve complete of oval flanges with mounting bolts, gasket, etc | Noted.
35 | Page 9 | 01 | Closed | Pressure norm. 22.1 bar(g) Temp. Norm.: 60°C Design temp. 157°C | Modified.
36 | Page 10 | 01 | Open | Design temp. 75°C->116°C Setpoint HH -> 34bar(g) | The original DT is correct according to PID. Setpoint was modified to the correct value.
37 | Page 11 | 01 | Open | Calibrated range: should be mentioned. -1...?? Clarify | This will be updated after the instrument is ordered. The -1 is required minimum range
38 | Page 12 | 01 | Open | As per project specification, thermowells shall be installed at least on 6" line size. | Please comment this on the P&ID.
39 | Page 12 | 01 | Open | Line Number, Area classification, PID number | See comment no. 9.
40 | Page 12 | 01 | Open | Plz check element type again | According to project specifications, type K is needed.
41 | Page 12 | 01 | Closed | Design temp: 65 -> 75°C | Modified.
42 | Page 12 | 01 | Open | Area classification -> Enclosure class | see comment no. 28
43 | Page 12 | 01 | Open | clarify the reason for the bracket | The transmitter is separate from the element, and it needs its own mount
44 | Page 12 | 01 | Open | Should be finalized and specified (For all TT) and relevant catalogs and order code should be submitted. | see comment no. 16
45 | Page 13 | 01 | Closed | Tag number change | Noted.
46 | Page 13 | 01 | Closed | Design temp. 65->75°C | Modified.
47 | Page 13 | 01 | Open | - Flange Type/rating/Facing/size/face finish should be mentioned. - Well Dimensions(Bore Diameter/Tip thickness/Immersion length/insertion length/... should be mentioned. | Noted, the datasheet will be updated once it's decided.
48 | Page 13 | 01 | Closed | Element tag number change | Changed to correct tag
49 | Page 13 | 01 | Open | plz clarify which part of TE/TW/TT . | The cable between the element and the transmitter.
50 | Page 13 | 01 | Open | Should be finalized and specified (For all PT) and relevant catalogs and order code should be submitted. | see comment no. 16
51 | Page 13 | 01 | Open | Thermowell wake Frequency calculation to be provided by vendor prior thermowell manufacture.Vendor ensures that the thermowell design is robust enough to cope with varying stresses and strains produced by the process media. | Noted.
52 | Page 16 | 01 | Closed | Proccess condition changes (same for page 17) | Modified to the correct values.
53 | Page 18 | 01 | Closed | Norm. Pressure 30 bar(g) | Modified.
54 | Page 20 | 01 | Open | Design temp. 116°C | Original value is correct according to P&ID
55 | Page 21 | 01 | Open | Proccess condition changes | Original DT value is correct according to P&ID
56 | Page 22 | 01 | Closed | Some items in format data sheet TG is not related to TG, plz check and revised TG data sheet again. (lines 19-41) | Modified to the correct values.
57 | Page 22 | 01 | Closed | Tag number change | Noted
58 | Page 22 | 01 | Closed | Line Number, Area classification, PID number | See comment no. 9.
59 | Page 22 | 01 | Closed | Design temp. 65->75°C | Modified to the correct value.
60 | Page 22 | 01 | Open | Should be finalized and specified (For all TT) and relevant catalogs and order code should be submitted. | see comment no. 16
61 | Page 22 | 01 | Closed | Thermowell wake Frequency calculation to be provided by vendor prior thermowell manufacture.Vendor ensures that the thermowell design is robust enough to cope with varying stresses and strains produced by the process media. | see comment no. 51
62 | Page 24 | 01 | Closed | Proccess condition changes | Modified to the correct values.
63 | Page 25 | 01 | Closed | Proccess condition changes | Modified to the correct values.
64 | Page 26 | 01 | Closed | Proccess condition changes | Modified the design pressure. Original design temperature is correct according to P&ID.