## Resolution Sheet
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | detail drawings for coolers | 17735-23A
Item no. | Reference | Revision | Status | Client Comments | Airpack - IWS-Monjé reply | Client Reply #1 | Client Reply #1
1 | Page 1 | 02 | Open | Please note that datasheet shall be submitted for checking this doc. please submit datasheet. | Airpack reply: Datasheet is submitted. We need approval on this drawing in order to start production of the cooler. Currntly we are facing delays when we don’t receive approval | Noted.
2 | Page 1 | 02 | Open | -To check the DWG, it is suggested that vendor submit the created thermal file for saving time in checking of documentation. -General arrangement, bundle drawing should be submitted, as well. Also a data sheet shall be submitted with below data: -Shell and tube side fluid properties (e.g. fouling factors, viscosity, heat capacity,etc) -Fluid flow rates and phases(shell and tube side). -Exchanger designed duty. | - done, thermal data sheet submitted during offer pahse - done, additional information on page3 - done, fulid properties able to see in the thermal data sheet - done, flow rates and phases able to see in the thermal data sheet - ASME | Noted.
3 | Page 3 | 02 | Open | In nozzle table, thickness/sch, and reinforcing pad dimensions shall be specified. | - done, nozzle thickness are acc. to. Standard - reinforcment pads are here not necessary | Noted.
4 | Page 3 | 02 | Open | Please add key plan and show the north direction. | Airpack reply: not needed to share on equipment drawings, able to see on GA. | Noted.
5 | Page 3 | 02 | Open | Please mention tube bundle data: -No of tubes -OD -thickness -tube straight length -pitch -layout -joint of tube to tubesheet -baffle cut/orientation. | - done , see page3 | Add this data as a table as well.
6 | Page 3 | 02 | Open | -Please mention that cooler is in accordance to TEMA C and please specify the type. -design code for wind and seismic calculation shall be specified. | - done, type specified - not sold or septified during the offer phase, no data sent. Airpack has a deviation for seismic and wind load. Airpack 23-Aug-2021: Considering the very small size of offered package, these loads are negligible and will therefore not be considered. We confirm package design is suitable to withstand such load cases. Nargan:Noted. | Noted.
7 | Page 3 | 02 | Open | -Please mention -joint efficiencies -No. of passes -RT for shell/tube (full/spot) -stress relieving (yes/No) -Insulation | - done in parts, no insoulation provided by manufacturer, see updated drawing | Noted. |  | Open
8 | Page 3 | 02 | Open | - done in parts, no insoulatio+F16n provided by manufacturer | - the fluid group describe the potential risks of the fluids acc. to the Directive 2014/68/EU as known as Pressure Equipment Directive (PED) - in your case not dangerous - not more necessary | Noted. |  | Closed
9 | Page 3 | 02 | Open | Design code for pressure test to be specified. | - done, pressure test acc. to. Standard | Noted.
10 | Page 3 | 02 | Open | Is it applicable for both coolers? | - done, both coolers are manufactured equal, the item number will be shown on the nameplate | Noted.
11 | Page 3 | 02 | Open | - type of bolt and required allowable stress in tension/shear to be specified. Please mention bolts are supplied by vendor. | - not in scope of supply, further information by Airpack -> Airpack reply: HEXAGONAL BOLT WITH THREAD UP TO THE HEAD DIN 933, STEEL 8.8 | it is in scope of airpack. Add this information to the drawing.
12 | Page 3 | 02 | Open | All weld details shall be added to the drawing. | - done, position of welding are now shown, further details in the welding documentation with the final documentation | No welding information is found.
13 | Page 4 | 02 | Open | Please also mention nut | - no nuts, flange has threaded holes | Noted.
14 | Page 4 | 02 | Open | please specify tie rods, spacers materials | - no tires and spacers are need in this design, material see 2D | Noted.
15 | Page 4 | 02 | Open | Please clarify about this. | - done, FYI: in his function, it's hold the bundle in place | Noted.
16 | Page 4 | 02 | Open | Please clarify about these material. they are unclear for us. material designation to be specified | - done, specificed | Noted.
17 | Page 4 | 02 | Open | ¦You are requested to recheck. Is material of shell, flange same? (usually, for shell, pipe/plate material is used while for flange, forge type is considered.) | - done, specificed | Please confirm that material of flange is forged.
18 | Page 4 | 02 | Open | material designation to be specified | - done | Noted.
19 | Page 4 | 02 | Open | For All Materials, please specify equivalent ASTM No. and grade. | - done | Noted.
20 | Page 4 | 02 | Open | Please provide drawings for specifying: shell thickness, tubesheet, flanges, covers details (thickness, dimentions), tube arrangement/layout, baffle details, tube bundle assembly, baffle spacing. | - done | noted.
21 | Page 4 | 02 | Open | Please clarify why for these elements same type material as tubesheet, tube, (SS) is not used. Please use SS. | - depending on material properties aluminium is choosen - Is there something specified for the air or why we should change this? | Since this exchanger is in your scope, material slection and guarantee of equipment is in vendor scope and the comments on material can be ignored.
22 | Page 4 | 02 | Open | Please recheck. This is not tube material. Please recheck since tubesheet is usually kind of plate or forged while tube material is not thiese kinds. | - done | Noted.
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37