## Resolution Sheet
PROJECT:
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Cause & effect chart | 17735-27
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 |  |  |  | Based on P&ID, compressor could be started or stopped from LPS and DCS. All signals should be shown here | It is all signals, can be changed from DCS to LSP with the local/remote switch and the tag is the same | Closed
2 |  |  |  | Based on Control philosophy, 320-HS-8206 will trip the compressor from DCS | Added | Closed
3 |  |  |  | IP-923 | Updated | Please revise based on new comment on C&E
4 |  |  |  | IP-920 | Updated | Please revise based on new comment on C&E
5 |  |  |  | IP-923 | Updated | Please revise based on new comment on C&E
6 |  |  |  | This document will be checked again after finalizing P&ID Reference document should be mentioned All tags in all documents should be the same format. | Noted, mentioned reference documents, change tags according to other documents. | noted.
7 |  |  |  | Please note that there is no safety comment on this document but the final approval shall be checked after HAZOP meeting. | We will update all the documents to AS BUILT so the latest version is provided. |  |  |  | Open
8 |  |  |  | C & E related to Running/fault/operational light, should be added. | The indication lights related to this signals are added. The functioning of the indication lights is described in the control philosophy. |  |  |  | Closed
9 |  |  |  | To be in two separate columns | Updated
10 |  |  |  | IP-920 | Updated
11 |  |  |  | IP-923 | Updated
12 |  |  |  | IP-920 | Updated
13 |  |  |  | Please specify in witch case PCV is closed / open | Updated, for information. When energized the PCV is constant opening and closing the bypass to keep the outlet pressure constant. When not energized it is in the fail position
14
15
16
17
18
19
20