## Resolution Sheet
PROJECT:
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Cause & effect chart | 17735-27
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 |  |  | Closed | Based on P&ID, compressor could be started or stopped from LPS and DCS. All signals should be shown here | It is all signals, can be changed from DCS to LSP with the local/remote switch and the tag is the same | Closed
2 |  |  | Closed | Based on Control philosophy, 320-HS-8206 will trip the compressor from DCS | Added | Closed
3 |  |  | Closed | IP-923 | Updated | Please revise based on new comment on C&E
4 |  |  | Closed | IP-920 | Updated | Please revise based on new comment on C&E
5 |  |  | Closed | IP-923 | Updated | Please revise based on new comment on C&E
6 |  |  | Closed | This document will be checked again after finalizing P&ID Reference document should be mentioned All tags in all documents should be the same format. | Noted, mentioned reference documents, change tags according to other documents. | noted.
7 |  |  | Closed | Please note that there is no safety comment on this document but the final approval shall be checked after HAZOP meeting. | We will update all the documents to AS BUILT so the latest version is provided. | Closed |  |  | Open
8 |  |  | Closed | C & E related to Running/fault/operational light, should be added. | The indication lights related to this signals are added. The functioning of the indication lights is described in the control philosophy. | Closed |  |  | Closed
9 |  |  | Closed | To be in two separate columns | Updated | Closed
10 |  |  | Closed | IP-920 | Updated | Closed
11 |  |  | Closed | IP-923 | Updated | Closed
12 |  |  | Closed | IP-920 | Updated | Closed
13 |  |  | Closed | Please specify in witch case PCV is closed / open | Updated, for information. When energized the PCV is constant opening and closing the bypass to keep the outlet pressure constant. When not energized it is in the fail position | Closed
14 |  |  |  | These signals are not found in PID | Incase of a trip the failure status signal is displayed. When there is no trip the available status is shown.
15 |  |  |  | Activation of "Available" signal with START command to be rechecked | Compressor can be started, running in unload and therefor be available. Comment is added that is will not be energized when the compressor is in load.
16 |  |  |  | Based on control philosophy, after each shutdown, compressor will be "available" after a "Restart Delay Timer". | Note is added
17
18
19
20