## Resolution Sheet
PROJECT:
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Cause & effect chart | 17735-27
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 |  |  | Closed | Based on P&ID, compressor could be started or stopped from LPS and DCS. All signals should be shown here | It is all signals, can be changed from DCS to LSP with the local/remote switch and the tag is the same | Closed
2 |  |  | Closed | Based on Control philosophy, 320-HS-8206 will trip the compressor from DCS | Added | Closed
3 |  |  | Closed | IP-923 | Updated | Please revise based on new comment on C&E
4 |  |  | Closed | IP-920 | Updated | Please revise based on new comment on C&E
5 |  |  | Closed | IP-923 | Updated | Please revise based on new comment on C&E
6 |  |  | Closed | This document will be checked again after finalizing P&ID Reference document should be mentioned All tags in all documents should be the same format. | Noted, mentioned reference documents, change tags according to other documents. | noted.
7 |  |  | Closed | Please note that there is no safety comment on this document but the final approval shall be checked after HAZOP meeting. | We will update all the documents to AS BUILT so the latest version is provided. | Closed |  |  | Open
8 |  |  | Closed | C & E related to Running/fault/operational light, should be added. | The indication lights related to this signals are added. The functioning of the indication lights is described in the control philosophy. | Closed |  |  | Closed
9 |  |  | Closed | To be in two separate columns | Updated | Closed
10 |  |  | Closed | IP-920 | Updated | Closed
11 |  |  | Closed | IP-923 | Updated | Closed
12 |  |  | Closed | IP-920 | Updated | Closed
13 |  |  | Closed | Please specify in witch case PCV is closed / open | Updated, for information. When energized the PCV is constant opening and closing the bypass to keep the outlet pressure constant. When not energized it is in the fail position | Closed
14 |  |  | Closed | These signals are not found in PID | Incase of a trip the failure status signal is displayed. When there is no trip the available status is shown. |  | closed
15 |  |  | Closed | Activation of "Available" signal with START command to be rechecked | Compressor can be started, running in unload and therefor be available. Comment is added that is will not be energized when the compressor is in load. |  | closed
16 |  |  | Closed | Based on control philosophy, after each shutdown, compressor will be "available" after a "Restart Delay Timer". | Note is added |  | closed
17 |  |  | Closed | Based on PID: Operational YL-8202 discrepancy with PID shall be removed | Available signal is not the operational or fault signal. Available signal is a signal to the DCS to see if the package is available. In case of a trip it will not be available, which can be seen then in the DCS. The C&E is updated that this is more clear |  | closed
18 |  |  | Closed | Based on PID: FAULT XA-8203 discrepancy with PID shall be removed | Fault and operational is added. But please note that the functioning is described in the control philosophy |  | closed
19 |  |  | Closed | It seems shall be "Unload". Please recheck | Checked and modified |  | closed
21 |  |  | Closed | Shall be 320SW-8206 As per Control philosophy document | updated |  | closed
22 |  |  | Closed | There is not any Failure signal in PID | agreed, signal is removed, since it is not used in the logic anymore. We have the trip siganl to see that the package is tripped and the fault signal to see that there is a fault in the package. All signals from the P&ID are updated to the C&E |  | closed
23 |  |  | Closed | As per other documents, all dash shall be deleted, for example 320XA-8203 | updated |  | closed
24 |  |  | Closed | DE and E has no meaning for "light". | updated |  | closed
25 |  |  | Closed | should be "X" | updated |  | closed
26 |  |  | Closed | These signals cause "Alarm" at DCS and are not "fault" | From rev.05 of the P&ID an attachment is send from your side with a request to have the following lights; - running - fault - operational - emergency trip In the meeting after we agreed to use the alarms for the fault signal. Therefor the fault is also shown 'amber' and not red as the trip light |  | closed
27 |  |  | Closed | These alarms do not affect the fault light | see above comment |  | closed
28 |  |  | Open | There is no hand switch for start from DCS. Compressor will be started by PALL-8191 or by HS from LCP | Please recheck this. Since this is since the first revision in the project documentation. If there is no remote control of the package, we will remove the following; - Start button DCS - Stop button DCS - ESD button DCS - Local / remote switch Please confirm, then we will updated all realted documents.