## Resolution Sheet
|  |  |  | PROJECT: | Integrated Methanol and Ammonia Plant
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Loop Diagrams | N-278-VD-6019-EL-DIA-0031-01
Item no. | Page | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 | 1 | 01 |  | the mentioned data in This document is for cable connection Diagram so shall be changed to Loop diagram. sample of loop diagram is available in attachment file. The loop diagrams document will be checked in next revision. | Airpack uses Eplan to generate Loop Diagrams using our own template, We use this template since no template was provided by the contractor during the sales phase. Template may only be slightly modified. | Noted. This document should be updated after finalizing PID and Wiring diagram document.
2 | 4 | 01 |  | with shroud | Updated.
3 | 4 | 01 |  | hot deep galvanaized | Updated.
4 | 6 | 01 |  | Tag should be modified , Refer to PID Comments | Updated.
5 | 7 | 01 |  | signal /command to be mentioned | Updated.
6 | 8 | 01 |  | signal /command to be mentioned | Updated.
Open
7 | 1 | 02 |  | - This document should be revised after the finalization PID and Wiring diagram document if needed. - Please issue the next Rev. after the finalization PID and Wiring diagram document | Noted. | Noted.
8 | 7 | 02 |  | based on comments on wiring diagram this page shall be modified | Updated. | Noted.
9 | 8 | 02 |  | should be modified As per comment wiring diagram document | Updated. | Noted.
10 | 8 | 02 |  | 1BK | Updated. | Noted.
11 | 8 | 02 |  | 2BK | Updated. | Noted.
12 | 8 | 02 |  | 3BK | Updated. | Noted.
13 | 8 | 02 |  | 4BK | Updated. | Noted.
14 | 1 | 03 |  | This document should be updated as per latest comment on wiring diagram LCP and JB document. | Updated. | Noted
15 | 4 | 03 |  | As per latest VPIS, "01" is removed from all document No. | Updated. | Noted
16 | 4 | 03 |  | BLACK | Updated. | Noted
17 | 4 | 03 |  | WHITE | Updated. | Noted
18 | 4 | 03 |  | BLACK | Updated. | Noted
19 | 7 | 04 |  | MCC | Updated.
20 | 9 | 04 |  | MCC | Updated.
21 | 1 | 05 |  | As per IO List comment , Loop diagrams should be updated. (related to the signal (AI or DI) for positioner feedback (PCV-8201) ) | Updated. | Noted. 320PZLC-8201 Tag name is Approved. Please ignore comment of related to "replacing of tag name PZLC to PZT" in logic block diagram document.