## Resolution Sheet
PROJECT:
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | PSV datasheet | 17735-46
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 | Page 1 | 01 | Closed | General comments 1- Any changes in next revision to be marked with revision mark. 2- If any comments is not applicable please send reply sheet. 3- Compatibility with project requirement is vendor responsibility and scope, and next comments are just for hint. 4- Compatibility with other vendor documents including PID and purchased instrument is vendor responsibility and scope. 5- Tag plate supply is scope of vendor and should added to data sheet as one of items. 6- all Tag name in all document should be same format. no needs "-" after prefix 320. example correct format is 320PSV-8201, ... . 7- For all instrument and accessories, catalogue(including order code) should be submitted . 8- all "VTA" status on document shall be finalized and specified . 9- This document will be checked after finalizing PID document. | 1. changes are marked in yellow 4. Datasheet is according to the P&ID 5. Added 6. Modified to this format. 7. Order code will not be submitted. 8. VTA will be finalized after ordering. | Noted. Order code to be specified and submitted after finalizing purchased instrument by sub-vendor. correct order selection is vendor responsibility.
2 | Page 4 | 01 | Closed | Line number/Area classification should be added | Added. | Noted.
3 | Page 4 | 01 | Closed | according spec of project should be full nozzle | Modified to this | Noted.
4 | Page 4 | 01 | Closed | P&ID number change | Changed | Noted.
5 | Page 4 | 01 | Closed | Bonnet connection: shall normally be flanged with facing and rating in accordance with the Piping Specification | Noted, modified bonnet connection to bolted type | Noted.
6 | Page 4 | 01 | Closed | Blow-Down should be mentioned. | Noted | Noted.
7 | Page 4 | 01 | Closed | Units should be mentioned / Specify the pressure unit | Noted |  |  |  | Open
8 | Page 4 | 01 | Closed | Lines 27-29 shall be finalized and specified. | It will be provided after ordering | Noted. |  |  | Closed
9 | Page 4 | 01 | Open | All PSV Sizes will be finalized after the approval Instrument calculation sheet document. | Noted | Noted.
10 | Page 4 | 01 | Closed | Valve body's material and connections shall be in accordance with Piping Class specifications | Noted | Noted.
11 | Page 4 | 01 | Closed | Seat and Disc / Nozzle materials as per spec of project should be SS316 | Noted. | Noted.
12 | Page 4 | 01 | Open | Manufacturer/Model should be finlaized, order code should be submitted. | After the valves have been ordered the datasheet will be updated with the manufacturer and model number. The valves will come from the approved vendor list, but we cannot provide the order code. | Noted.
13 | Page 5 | 01 | Closed | Max allowable relief pressure: 30.5 x 1.1+1.013=34.56 bara | Modified to the correct value
14 | Page 6 | 01 | Closed | Max allowable relief pressure: 39 x 1.1+1.013=43.91 bara | Modified to the correct value
15 | Page 7 | 01 | Closed | Process condition value changes | Modified to the correct value
16 | Page 7 | 01 | Closed | Recheck connection inlet: #150 | Rechecked, it is correct
17 | Page 1 | 02 | Open | - This document will be reviewed again after PSV ordering. - All PSV Sizes will be finalized after the approval Instrument calculation sheet document. | Noted.
18 | Page 4 | 02 | Closed | All materials should be approved by sub-vendor after as per process fluid conditions. This comment to be consider for all applicable per case | Noted, added to datasheet as note.
19 | Page 4 | 02 | Closed | Sizing calculation: Should be mentioned yes | Noted, updated
20 | Page 7 | 02 | Closed | According to meeting tube rupture scenario shall be considered for this PSV (8204) | Noted, updated
21 | Page 7 | 02 | Open | clarify why CS is considered for PSV-8204 | This is according to the PO.
22 | Page 7 | 02 | Open | Norm. Process temperature 36 -> 46 | According to P&ID, 46°C is the max temperature.
23
24
25