## Resolution Sheet
|  |  |  | PROJECT: | Integrated Methanol and Ammonia Plant
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Valve datasheet CRS | N-278-VD-6019-IN-DS-0041-01 (17735-48)
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 | Page 1 | 01 | Closed | General Comment: 1- Any changes in next revision to be marked with revision mark. 2- If any comments is not applicable please send reply sheet. 3- Compatibility with project requirement is vendor responsibility and scope, and next comments are just for hint. 4- Compatibility with other vendor documents including PID and purchased instrument is vendor responsibility and scope. 5- Tag plate supply is scope of vendor and should added to data sheet as one of items. 6- all Tag name in all document should be same format. no needs "-" after prefix 320. example correct format is 320PCV-0170, ... . 7- For all instrument and accessories, catalogue(including order code) should be submitted . 8- This document will be checked after finalizing PID document. 9- Manufacturer, Model, order code for all instrument should be finalized and specified, Also relevant catalogs and order code should be submitted. Important Note: Next revision of instrument data sheet shall be submitted after PID finalization | Noted. 1. Changes are marked with yellow background 6. All documents follow the format specified on the P&ID. 7. Order code cannot be provided | Noted. Order code to be specified and submitted after finalizing purchased instrument by sub-vendor. correct order selection is vendor responsibility. | The order code will not be submitted in this document.
2 | Page 1 | 01 | Closed | Document title: To be revised based on document content | Noted
3 | Page 1 | 01 | Open | SIL & HAZOP study Consequences, shall be implemented in this document. | The SIL and HAZOP study consequences will not be noted in the datasheet. From the 3rd party study a report is generated where all details can be found. | This means that the SIL & HAZOP study results should be considrered in the data sheets item. Example TT is sil2 or 3 | Noted. The datasheet will be updated according to the SIL&HAZOP study, once it is available.
4 | Page 3 | 01 | Closed | All "-"(After320) should be deleted in all of Tags. | Noted, modified. | Noted
5 | Page 3 | 01 | Closed | only 320PCV-8201 is instrument valve. other vale is related to piping valve and should be removed from this document. | The document title will be revised | Noted. Should be revised.
6 | Page 4 | 01 | Closed | Design temp 65°C->75°C | Modified
7 | Page 6 | 01 | Closed | Design temp 65°C->75°C | Modified. |  |  |  | Open
8 | Page 7 | 01 | Closed | Norm. Pressure: 5->2,5bar(g); Design temp: 65->75°C | 2,5 barg is minimum pressure, operating pressure is 4,4 barg |  |  |  | Closed
9 | Page 8 | 01 | Closed | PCV or PV ? should be clarify . PCV do not receive electrical signals | It does receive electrical signals. | Noted
10 | Page 8 | 01 | Closed | Line number / Area classification should be added | Added | Noted
11 | Page 8 | 01 | Closed | PID number change | Modified | Noted
12 | Page 8 | 01 | Closed | Norm. Pressure: 9,5bar(g)->30bar(g) | Modified
13 | Page 8 | 01 | Closed | Bonnet shall be bolted according to ASME B31.3 and material shall be the same as the body material. | Noted, modified. | Noted
14 | Page 8 | 01 | Closed | Flange Face Finish should be mentioned | Added | Noted
15 | Page 8 | 01 | Closed | should be added, - Characteristics - Cage material | Added | Noted
16 | Page 8 | 01 | Closed | should be added, Positioner material. Enclosure Class . Manufacturer. | Added | Noted
17 | Page 8 | 01 | Closed | All Positioners must have the following capabilities; - Modular design - Auto tuning (software) - Fail- Safe or Fail-Freeze output (Software) - Operating panel LCD - With supply/ output pressure gauge | The positioners will be chosen according to the specifications. I only found the gauge requirement, so that is added to the datasheet. | Noted
18 | Page 8 | 01 | Closed | Instrument air supply will be available at Minimum 4 bar g, Normal 8 bar g, Maximum 10 bar g, air quality according to ANSI/ISA-7.0.01 and design pressure at 12.5 bar g. | According to the P&ID, the valve is operated with the same instrument air that is used by the compressor. | As per previous comment Instrument Supply Fluid" pressure", should be considered as per minimum Instrument air supply 4 barg for proper actuator sizing. | Noted.
19 | Page 8 | 01 | Closed | Position monitor: this signal should be mentioned in PID | Noted. | Noted
20 | Page 8 | 01 | Closed | Filter regulator: Yes, stainless steel | Noted | Noted
21 | Page 8 | 01 | Closed | Mfr. & Model for air set should be mentioned. | Noted. | Noted
22 | Page 8 | 01 | Closed | Tubing, Fitting line to be added | Noted. | Noted
23 | Page 8 | 01 | Closed | PC Sizes will be finalized after the approval Instrument calculation sheet document. | Noted. | Noted
24 | Page 8 | 01 | Closed | Required Cv should be added | Noted. | Noted
25 | Page 8 | 01 | Closed | Leakage Class certificate | Noted. | Noted
26 | Page 8 | 01 | Open | Purchase info: Should be finalized and specified, relevant catalogs and order code should be submitted. | Purchase info will be finalized after order. The order code cannot be disclosed. | Noted
27 | Page 10 | 01 | Closed | The Tag No. of strainers should be shown on the PID. | It's already on the p&id
28 | Page 10 | 01 | Closed | 65°C -> 75 °C | Modified
29 | Page 11 | 01 | Closed | 65°C -> 75 °C | Modified
30 | Page 8 | 02 | Closed | Cable gland: safe area to be corrected | Modified
31 | Page 8 | 02 | Closed | Materials should be added | Added
32 | Page 8 | 02 | Closed | Order code to be specified and submitted after finalizing purchased instrument by sub-vendor. this comment to be consider for all applicable per case | The order code will not be submitted in this document.
33
34