## Resolution Sheet
PROJECT:
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Valve datasheet CRS | N-278-VD-6019-IN-DS-0041-01 (17735-48)
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 | 8 | 05 |  | - Control valve and all accessories catalogue(including order code) should be submitted . - sub-vendor control valve calculation to be added this document. - proper sub-vendor and order code selection is vendor responsibility. | - Catalogue will not be provided. The necessary information will be included in The databook in the final stage. - All the necessary information is provided. - Noted. | Noted.
2 | 8 | 05 |  | As per piping material class specification, should be 300# | Noted. It will be updated. | Noted.
3 | 8 | 05 |  | to be filled | Noted. It will be updated. | Noted.
4 | 8 | 05 |  | As per catalog, BODY AND SPRING CASE is not SS. check and modify, plz correct model No. | Filter regulator information will be updated. | Filter regulator Shall be SS316 and model Shall be modified. | Updated
5 | 8 | 05 |  | DVC (not DCV) is correct, complete order code should be mentioned. | Noted. It will be updated. | Noted.
6 | 1 | 06 |  | Please move 320PCV-8201 and SG-8201, SG-8202 to Instrument Data Sheets (N-278-VD-6019-IN-DS-0013) | The PCV will remain in this datasheet, as it is a valve. The sight glasses will be moved to the as built version of the instrument datasheets
7 | 19 | 06 |  | glass should be tempered | The glass is borosilicate. |  |  |  | Open
8 | 19 | 06 |  | to be filled | Noted. Updated |  |  |  | Closed
9
10