## Resolution Sheet
|  |  |  | PROJECT: | Integrated Methanol and Ammonia Plant
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Instrument Cable Schedule | N-278-VD-6019-IN-SCH-0044-01 (17735-52)
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 | 3 | 01 |  | This document should be revised based on latest comments of relevant Documents (Wiring Diagram (including Terminal Diagram) for LCP Panel and Junction Box). | Noted. This document is updated according to per latest wiring diagram. | noted. Refer to comments on The latest revision of the document
2 | 3 | 01 |  | Plz Next revision of instrument data sheet shall be submitted after Wiring Diagram document finalization. | Please put the comment in the correct document. This cable schedule is updated according to per latest wiring diagram. | Noted.
3 | 3 | 01 |  | Compatibility with other vendor documents including PID and Wiring diagram is vendor responsibility and scope. | Noted. | Noted.
4 | 3 | 01 |  | Cable code identification should be mentioned as per spec of project.(Attachment#1) | Noted. Cable code will be added. | Noted.
5 | 3 | 02 |  | cable type to be 20C1.501ARGYN | Updated to 14C1.501ARGYN based on comments provided on the wiring diagram. | Noted.
6 | 3 | 02 |  | cable type to be 4C1.501ASRDN | Updated. | Noted.
7 | 3 | 02 |  | cable type to be 19P0.7511ARGYN | Updated. | Noted. |  |  | Open
8 | 3 | 02 |  | cable type to be 1P1.501ARGYN | Updated. | Noted. |  |  | Closed
9 | 3 | 02 |  | these glands on JB or local panel so are in vendor scope of work. Please specift gnald size. | This is not correct, the document states that these glands are on the customer's side and therefor not in Airpack's scope. This information should be provided by the contractor. Changed to TBA (To Be Advised). | All materials in skid limits are vendor scope. As per TCL, only Instrument multi-Cables from control room(MCC) to Junction Boxes(or LCP) are in client scope of work. | As per the document, these cables run FROM the customer, TO Airpack. Thus, the glands in the fourth column relate to the location stated in the third column, which states FROM the CUSTOMER/MCC. This is NOT in Airpack scope, but in the scope of th CLIENT. In the 9th column are the glands that realte to the location stated in the 6th column, which is the LCP and the JB. This is in Airpack's scope, and that is why we were able to give the gland sizes for this side of the cable. We CANNOT provide the gland sizes and the glands for the end of the cable at the client's side. This is not as per the purchase order. It is also NOT in Airpacks scope to install these cables or these glands. Please provide the sizes of the glands or it will be left as TBA. If this is still unclear, please arrange a meeting with the technical project manager at Airpack so that Airpack can explain the document for further clarity.
10 | 3 | 02 |  | cable length to be added in table | Updated. | Noted.
11 | 3 | 02 |  | This document should be updated as per latest comment on wiring diagram LCP and JB document. | Updated. | Noted.
12
13 | 3 | 03 |  | these glands on JB or local panel so are in vendor scope of work. Please specify gland size.(As per Outline Dimensional Drawings document) | As per the document, these cables run FROM the customer, TO Airpack. Thus, the glands in the fourth column relate to the location stated in the third column, which states FROM the CUSTOMER/MCC. This is NOT in Airpack scope, but in the scope of th CLIENT. In the 9th column are the glands that realte to the location stated in the 6th column, which is the LCP and the JB. This is in Airpack's scope, and that is why we were able to give the gland sizes for this side of the cable. We CANNOT provide the gland sizes and the glands for the end of the cable at the client's side. This is not as per the purchase order. It is also NOT in Airpacks scope to install these cables or these glands. Please provide the sizes of the glands or it will be left as TBA. If this is still unclear, please arrange a meeting with the technical project manager at Airpack so that Airpack can explain the document for further clarity. | Noted
14 | 3 | 03 |  | 12C-2.5 | This comment cannot be incorporated as the cable size given in the wiring diagram is different and the wiring diagram has already been approved. If this needs to be changed, first provide a comment in the wiring diagram.
15 | 3 | 03 |  | 5C-2.5 | This comment cannot be incorporated as the cable size given in the wiring diagram is different and the wiring diagram has already been approved. If this needs to be changed, first provide a comment in the wiring diagram.
16 | 3 | 03 |  | MCC | Updated.
12
18 | 3 | 05 |  | 12X2.5 | In revision 2 it was requested that this cable be changed to a 20Cx1.5mm². In revision 4 it was requested that this cable be changed to a 14Cx1.5mm². Now you are requesting that this cable be changed to a 12Cx2.5mm². This change will not be implemented and the wiring diagram will kept as is (It was previously approved, only the position feedback was added), and it is kindly requested that you again approve this document. Constant changes and comments are preventing this project from moving forward and is not allowing us to order the necessary parts which will ultimately delay the entire project. | Noted. Sorry for inconvenience There was a discrepancy between Nargan Elec. and CNI Dpt understanding of control philosophy. Please implement our minor comment on page No. 3
19 | 3 | 05 |  | 5X2.5 | This change will not be implemented and the wiring diagram will kept as is (It was previously approved, only the position feedback was added), and it is kindly requested that you again approve this document. Constant changes and comments are preventing this project from moving forward and is not allowing us to order the necessary parts which will ultimately delay the entire project. | Noted. Sorry for inconvenience There was a discrepancy between Nargan Elec. and CNI Dpt understanding of control philosophy. Please implement our minor comment on page No. 3
20