## Resolution Sheet
|  |  |  | PROJECT: | Integrated Methanol and Ammonia Plant
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Wiring Diagram | N-278-VD-6019-IN-DIA-0005-01
Item no. | Page | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 | 1 | 01 |  | - This document should be submitted after finalizing P&ID, I/O List and Outline Dimensional Drawings documents . - Plz find other comment in next pages. | - Document submitted as per VDS. - Noted. | Will be checked again after finalizing PID, Compatibility with other vendor documents including PID, IO List, Outline Dimensional Drawings, ...is vendor responsibility and scope. | Noted.
2 | 6 | 01 |  | As per project specification, Tag LCP should be modified to "300LP-820" | Tag correct as per P&ID. If tag is not correct according to project specification, please make comment in the P&ID first, tag will then be updated in the wiring diagram and all other subsequent documentation. | Noted. It is commented in last PID | Noted.
3 | 6 | 01 |  | symbol and legend should be added. | Added symbol legend. | Noted.
4 | 7 | 01 |  | - Cable for all digital signals should be multi core - Tag cable : will be checked after finalizing data sheet document , (IS or NIS instrument should be determined in data sheet document) | - Cable changed to multicore cable. - It has already been determined that all instruments are non Ex instruments (installed in safe area) and are NIS. - If tag cable is not correct, please provide correct cable tag in order to avoid confusion and reduce project delays. | -Noted -Noted -It is mentioned in new comment | Noted.
5 | 7 | 01 |  | terminal tag should be follow spec of project | Terminal tags updated, if terminal tags are not correct, please provide correct tag in order to avoid confusion and reduce project delays. | -It is mentioned in new comment | Noted.
6 | 7 | 01 |  | As project spec : Following colors shall be used for identification:  Single and multi core: Black types of instrumentation cables :  Analogue cables (multi & single pair)  Digital cables (multi & single core) | Updated as per porject spec. | -It is mentioned in new comment | Noted.
7 | 7 | 01 |  | from MCC following signals will be sent to LCP via free voltage contact: 1- run 2- fault 3- available vendor to consider them inside LCP | According to P&ID, there will be no MCC signals in the LCP. The LCP only has lamps and buttons. The entire package is controlled by the DCS of the customer. | signals means the contact for the signal lamps.run , fault , available will send to lcp for operating the signal lamps | Comment unclear, if lamp signals are not correct, please comment on the P&ID and the control philosophy. The wiring diagram will then be updated accordingly. |  | Open
8 | 13 | 01 |  | As per project specification, Tag JB(LCP) and tag cable should be modified. For NIS signal Analog : 300JDAN-820/300CDAN-820 For IS signal Analog : 300JDAI-820 (If any) | Cable tag updated. Junction box tag kept the same as the tag on the P&ID for reasons mentioned earlier. All signals NIS. | Refer to Item 2 | Noted.
9 | 13 | 01 |  | Should be Modified .(19x2x0.75) | Updated. | Noted
10 | 4 | 02 |  | with | Updated.
11 | 4 | 02 |  | hot dipp galvanized | Updated.
12 | 7 | 02 |  | RE-comment: As per project specification, Tag LCP should be modified to "300LP-820" | Updated.
13 | 7 | 02 |  | General Note: General Comment: 1- Any changes in next revision to be marked with revision mark. 2- If any comments is not applicable please send reply sheet. 3- Compatibility with project requirement is vendor responsibility and scope, and next comments are just for hint. 4- Compatibility with other vendor documents including PID, IO List, Outline Dimensional Drawings, ...is vendor responsibility and scope. 5- This document will be checked again after finalizing PID document. 6- all Tag name in all documents should be same format. no needs "-" after prefix 320. example correct format is 320TT-8201, ... . | 1 - It is not possible to mark revisions changes in Eplan. 2 - CRS is always sent, as above. 3 - You're package will be manufactured according to the approved project documents. 4 - Noted. Every effort is made to ensure all project documents are aligned. 5 - Noted. 6 - Updated. | 1 - clarify !!!! In all revision eplan software from Eplan 5.5 to P8 electrical or propanel , you can mention revision mark. For The easiest way, plz refer to PDF file. 2- Noted 3 - Contractor's comments do not relieve, in any case, Vendor from their responsibilities. 4 - Noted 5 - Noted 6 - Noted
14 | 7 | 02 |  | 300TDD820 | Updated. | Noted
15 | 7 | 02 |  | 300TED820 | Updated. | Noted
16 | 8 | 02 |  | Local/Remote - should be checked and clarify. one signal is considered in IO list document for local /Remote. | Updated. | Noted
17 | 8 | 02 |  | Clarify why off position is used ? | Updated to two position switch without off position. | Noted
18 | 8 | 02 |  | Incompatible with legend, two or three position? | Updated to two position, legend also updated. | Noted
19 | 8 | 02 |  | As project spec : Following colors shall be used for identification:  Single and multi core: Black types of instrumentation cables :  Analogue cables (multi & single pair)  Digital cables (multi & single core) | Noted. | Single and multi core: Black for all digital signal. Emergency push button is missed. Plz modify
20 | 8 | 02 |  | 1 BK | Updated. | Noted
21 | 8 | 02 |  | 2 BK | Updated. | Noted
22 | 8 | 02 |  | 3 BK | Updated. | Noted
23 | 8 | 02 |  | 4 BK | Updated. | Noted
24 | 8 | 02 |  | 20Cx1.5 mm2 | Updated. | Noted
25 | 8 | 02 |  | 300CDDN820 | Updated. | Noted
26 | 8 | 02 |  | 300TDD820 | Updated. | Noted
27 | 8 | 02 |  | All Tags should be modified(refer to general note) | Updated. | Noted
28 | 9 | 02 |  | these two signals are combined in MCC as fault | Lamp signals correct according to P&ID, if signals are not correct, please comment on the P&ID first.
29 | 9 | 02 |  | we do not have such a signal in MCC , only run , fault and available can be sent to package | Lamp signals correct according to P&ID, if signals are not correct, please comment on the P&ID first.
30 | 10 | 02 |  | 300TED820 | Updated. | Noted
31 | 10 | 02 |  | 300CED820 | Updated. | Noted
32 | 13 | 02 |  | 300TDA820 | Updated. | Noted
33 | 13 | 02 |  | 300TDA821 | Updated. | Noted
34 | 14 | 02 |  | 300CDAN820 | Updated. | Noted
35 | 14 | 02 |  | 300TDA820 | Updated. | Noted
36 | 14 | 02 |  | 320PT-8201 | Updated. | Noted
37 | 14 | 02 |  | should be modified (refer to general note) | Updated. | Noted
38 | 18 | 02 |  | 300TDA821 | Updated. | Noted
39 | 1 | 03 |  | - This document should be revised after the finalization PID and IO list document if needed. - Please issue the next Rev. after the finalization PID and IO List document - Lamp test Push button should be added, as per TCL, this comment should be implemented in PID document too. | Updated as per the latest P&ID.
40 | 9 | 03 |  | this signal is feeder available in MCC. which means feeder is not faulty and also mccb is not withdrawn | Updated as per the latest P&ID.
41 | 9 | 03 |  | there is just one fault signal from MCC to package | Updated as per the latest P&ID.
42 | 10 | 03 |  | Re commentAs project spec : Following colors shall be used for identification:  Single and multi core: Black | Updated.
43 | 10 | 03 |  | 1BK | Updated.
44 | 10 | 03 |  | 2BK | Updated.
45 | 10 | 03 |  | 3BK | Updated.
46 | 10 | 03 |  | 4BK | Updated.
47
48
49
50
51
52