## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 14/Dec/2021 | Rev.: 02
|  | Comment Sheet Ref.No.: | Doc Description: UCP/LCP/JB GENERAL ARRANGEMENT DRAWING & TERMINAL DETAILS FOR NITROGEN GAS BOOSTER INCL. BOM
|  | Transmittal No.: APCES-V-00068 | Doc. No.: BU-20-VD-303-IN-DWG-0039
|  | Transmittal Date: 14/12/2021 | Doc Rev.: 02
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply
1 | 7M11 |  |  | Updated in next revision |  |  | Closed.
2 | Quint diode module to be specified. Terminals to be specified |  |  | Updated in next revision |  |  | Closed.
3 | Quantity and model number column to be added and specified too. |  |  | Quantity added, model number will be included in the spare part list this is another document |  |  | Closed.
4 | Panel lifting lugs and its details to be specified. |  |  | Updated in next revision |  |  | Closed.
5 | Ventilation system fitted with dust filters and with extraction fans mounted on the top of cabinets shall be provided. |  |  | Fan outlet filter at the top and the fan motor is at the bottem |  |  | Fans motor shall be on the top of the panel and filter must be at the bottom of front door.
6 | To be separate to two earth bar ISE and NISE |  |  | ISE and Pe Bar check wiring diagram |  |  | PE is protective earth for panel earthing, for IS and NIS signals separate earth bar shall be considered.
7 | For JB drawing requirement such as name plate, tag plate, terminal arrangement and etc. please refer to attached file |  |  | Noted |  |  | Required data as per attached file was not implemented.(such as name plate, special label and etc.)
1 | 16 terminal |  |  | Confirmed |  |  | Closed.
2 | Terminal drawing detail same as attached file to be specified |  |  | Rear side can not be shown this is not part of the panel layout Confirmed separation of 24VDC and 230VAC in all trunking and ways |  |  | Closed.
3 | Please modify to 5x 1x is sufficient |  |  | Updated in next revision |  |  | Closed.
4 | (RAL 9006) Gray Refer to clause M33 of TCL Eex'd' to be considered |  |  | This is (RAL 6021) Green Eex 'e' junction box as per project specification for terminal junction boxes |  |  | According to selecting Eex'd' type solenoid valve, so selected JB shall be Eex'd' too. JB protection shall be considered Eex'd' and its color shall be RAL9006
5 | For JB drawing requirement such as name plate, tag plate, terminal arrangement and etc. please refer to attached file |  |  | Noted |  |  | Required data as per attached file was not implemented.(such as name plate, special label and etc.)
6 | 31 terminal |  |  | X2 has now 61 terminals |  |  | Closed.
7 | 1x is sufficient |  |  | Updated in next revision |  |  | Closed.
8 | EL-04: ammeter shall be considered. |  |  | Ammeter is mounted on the distribution panel check P&ID |  |  | Noted
9 | EL02: 1- The rear of the door shall be shown with mounted devices and wiring channel. 2-The suitable provision shall be considered for separation of 24Vdc and 230VAC in all trunking and ways. |  |  | Rear side can not be shown this is not part of the panel layout Confirmed separation of 24VDC and 230VAC in all trunking and ways |  |  | 1- Noted 2- Noted
10 | EL-03: The terminal Strip code is specified, but terminal numbers shall be add too. |  |  | Updated in next revision |  |  | Noted
11 | EL01: The technical specifications shall be completed in nameplate. The below items shall be added in name plate: -The degree of protection panel -The permissible withstanding short circuit current -The total weight of panel -The insulation voltage of panel -Manufacturer date -The panel tag |  |  | Confirmed |  |  | Vendor confirmed that but any actions have not been done on document.
12 | Modify the MC logo |  |  | Format is the same as the P&ID |  |  | MC logo shall be modifyed
13 | BU-20-VD-303-IN-DWG-0039 01 |  |  | Updated in next revision |  |  | Closed.
14
15 |  |  |  | Closed.O15:I3026
17
18
19
20
21
22
23
24