## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 03/Feb/2022 | Rev.:04
|  | Comment Sheet Ref.No.: | Doc Description: Calculation & Datasheet of Control valves / On-off valves for Nitrogen gas booster
|  | Transmittal No.: APCES-V-00091 | Doc. No.: BU-20-VD-303-IN-DSH-0041
|  | Transmittal Date: 03/Feb/2022 | Doc Rev.: 04
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply | vendor clarification | CES Reply
1 | All page of datasheet to be in project title block. |  |  | Format can't be changed for this document, however we will add contracter and client logo in each page.
2 | P&ID number to be modified as per related P&ID document number for all instruments. |  |  | Updated in next revision |  |  | Closed.
3 | Line number of each PSV shall be specified. |  |  | Updated in next revision |  |  | Closed.
4 | To be modified |  |  | Updated in next revision |  |  | Closed.
5 | Ambient |  |  | Updated in next revision |  |  | Closed.
4 | According to PID, solenoid valve as an accessories shall be considered for On-off valve. |  |  | According P&ID Solenoid valves have a seperate TAG-no. Thus considered as a seperate item with corresponding datasheet. |  |  | Solenoid valve's tag shall be same as its on-off valve's tag sequence. Solenoid valve is an important accessories in on-off valves so one section must be assigned for this issue and specified general data such as tag no., signal type, ex protection, area classification, material and etc. | Solenoid datasheet is part of 17811-12A Instrument datasheets. Cross-reference updated on next revision. | Closed.
5 | Leakage class shall be specified. |  |  | Updated in next revision |  |  | Comment is not implemented in the document. | updated in next revision | Closed.
6 | Trim, seat, ball, stem etc.material shall be specified. |  |  | Updated in next revision |  |  | Project PMS as mentioned in the document shall be followed by vendor. | updated in next revision | Closed.
7 | Please clarify why 2 pneumatic connection is required. |  |  | This is standrad for pneumatic actuator, for single action 1x will be used, for double acting 2x will be used. |  |  | Noted, Closed.
8 | Actuator yoke and housing shall be carbon steel. |  |  | Rack&pinion type actuator do notvhave a yoke and casrbon steel housing is not available. Aluminium epoxy coated is Airpack standard and suitable for this application en evironment. |  |  | Noted, Closed with vendor guarantee for environmental condition. | noted | Closed.
9 | Recheck |  |  | Updated in next revision |  |  |  |  | Closed.
10 | Nitrogen |  |  | Updated in next revision |  |  |  |  | Closed.
11
11 | PV-10151 datasheet and calculation sheet shall be added. |  |  | Updated in next revision (calculation sheet VTA) |  |  | Closed.
12 | Revised P&ID shall be issued before this document, latest revision of P&ID (rev.1) has not confomity with instrument datasheet. |  |  | Updated in next revision |  |  | Closed.
13 | Tag no shall be revised as per latest rev. of PID |  |  | Updated in next revision |  |  | Closed.
14 | All check valve and hand valve shall be deleted. |  |  | There is no other document for this, so they will be kept here and they need to be checked. |  |  | There is no need to submit data of manual valve and check valve. There is no need to add any document regarding manual valve and check valve in VPIS. It is in airpack responsibility to purchase all valves as per project requirements.Data of manual valve and check valve shall be removed.
15 | These valves will not be checked… |  |  | See comment 14 |  |  | See item 14
16 | Based on Basis of design of design pressure ….. |  |  | design pressures are as per P&ID. |  |  | PR Reply: Design pressure must be calculated based on Project Criteria.
17 | 500C(N) |  |  | 501C(N) as per P&ID |  |  | PR Reply: Based on Project Criteria it must be considered 500C(N)
18 | 7 |  |  | Updated in next revision |  |  | PR Reply: Closed.
19 | 100 |  |  | 95 as per P&ID will be updated |  |  | PR Reply: Closed.
20 | Not found on PID |  |  | Updated in next revision |  |  | PR Reply: Closed.
21 | Tag no shall be revised |  |  | See comment 13 |  |  | Closed.
22 | Flow rate of both cooling waters are 14,5 m3/h. Flow rate of main cooling water header must be double checked. |  |  | This is correct, total cooling water flow is 14,5 m3/hr |  |  | PR Reply: Closed.
23 | Ex'd' certificate for solenoid valve is required |  |  | see comment 4 |  |  | Closed.
24 | Please clarify it is not found in PID |  |  | It is the filter symbol at the Compressor Inlet upstream solenoid XY-10151 |  |  | Tag no shall be specified, also mentioned in P&ID too.
25 | 85 |  |  | 80 as per P&ID |  |  | PR Reply: Design pressure must be calculated based on Project Criteria.
26
26 | Hand valves and check valves will not checked by instrument department and shall be removed from this data sheet. |  |  | It is customer responsibility to check this, if not checked we will assume it is approved. And continue with ordering. |  |  | It is in vendor responsibility to supply all instrument, component, piping , equipment and etc. based on project requirements. However, see the comments inside of documents.
27 | ALL MANUAL VALVE AND CHECK VALVE SHALL BE DELETED. PROJECT SPECIFICATIONS SHALL BE FOLLOWED BY AIRPACK. |  |  | See item 26 |  |  | See item 26
28 |  |  |  | Design pressures are as per design pressures on the P&ID, as there were no comments on the P&ID, the same design pressure will be followed. |  |  | Compressor operating pressure is 23.5 bara. Therefor,25 bara for operating pressure shall be deleted. PSV set pressure as per P&ID is 25barg.
29 | Design pressure must be double checked |  |  | See item 28. |  |  | See item 28
30 | 52 |  |  | 40°C as per P&ID |  |  | 52 oC as per the project data sheet
31 | 85 |  |  | Updated in next revision |  |  | Closed.
32 | 707 kg/h / 565 Nm3/h |  |  | Updated in next revision |  |  | Closed.
33 | 500C(N) |  |  | we will update to 500C(N) |  |  | Closed.
34 | Tag no shall be specified, also mentioned in P&ID too. |  |  | No tag nr. mentioned on P&ID |  |  | P&ID shall be revised in next revision. In order to check the data, tage number shall be specified in P&ID.
35 | Line no to be specified |  |  | No line no mentioned in P&ID |  |  | Line number shall be specified in P&ID.
36 | Body material based on ASTM code shall be selected as per line number class from the project PMS. |  |  | Updated in next revision |  |  | Closed.
37 | Following items shall be specified for control valve: CV, travel%, Trim characteristic |  |  | Mentioned in calculation; updated in revision after purchase. |  |  | Noted. Also calculation result shall be mentioned in data sheet
38 | Positioner required data such as follow shall be added to data sheet: Input signal, IP, Pneu.- elec. connection size. |  |  | Mentioned iin line 28, 30, 35 on datasheets. IP added in next revision. |  |  | Closed.
39 | Positioner shall included with pressure gauge |  |  | Updated in next revision. |  |  | Closed.
40 | Minimum material for wetted part shall be SS316. |  |  | Mentioned in line 21 datasheet. |  |  | Closed.
41 | 85 dBA |  |  | Updated in next revision. |  |  | Closed.
42 | Filter regulator and gauge are required |  |  | Updated in next revision. |  |  | Closed.