## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 14/Feb/2022 | Rev.:02
|  | Comment Sheet Ref.No.: | Doc Description: INSTRUMENT HOOK UP DRAWING FOR NITROGEN GAS BOOSTER
|  | Transmittal No.: APCES-V-00096 | Doc. No.: BU-20-VD-303-IN-DWG-0033
|  | Transmittal Date: 14/Feb/2022 | Doc Rev.: 02
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply | Vendor Clarification (2)
1 | this part is as internal part of valve and 1 integrated on / off valve including ball valve and related SOV will be supplied by vendor. But related instrument air tubing to be indicated in hook up from main header of inst air. |  |  | Intrument air air tubing is already shown. But from main header will be shown as "FROM COM. INLET". |  |  | Required connections to be specified in hook-up. | Noted.
2 | Related instrument air tubing to be indicated in hook up from main header of inst air. |  |  | Intrument air air tubing is already shown. But from main header will be shown as "FROM COM. INLET". |  |  | Please refer to attached file about air hook-up in the document. | Noted.
3 | 2 |  |  | Noted. It will be incorporated. |  |  | Closed.
4 | 8 |  |  | Noted. It will be incorporated. |  |  | Closed.
5 | Length to be specified |  |  | The tubing length is according to the actual engineering. It will not be shown. |  |  | Noted, by vendor responsibility.
6 | - Line service shall be specified.(liquid, gas, etc.) - Nozzle tap orientation shall be same as attached file, and specified in pressure hook-up pages. |  |  | - Noted. The line service will be specified. - The hookup drawing is as per Airpack standard. Nozzle tap orientation will not be shown. |  |  | - Closed. - Pressure hook-up for gas and liquid services shall be segregated and specified in different pages, because of in gas services, pressure tapping shall be in 12 o'clock of pipe and in liquid services, pressure tapping shall be in 6 o'clock of pipe, also tapping orientation shall be specified in pressure hook-up with figure or as a note.
7 | 1 |  |  | Noted. It will be incorporated. |  |  | Closed.
8 | 6 |  |  | Noted. It will be incorporated. |  |  | Closed.
9 | Tube and cap to be considered for drain /vent of manifold. |  |  | Noted. It will be incorporated. |  |  | Closed.
10 | - Air header and required connection to be specified. - Vendor to clarify, whether filter/regulator is required before solenoid valve. |  |  | - This is the compressor inlet solenoid valve on the instrument airline. Airheader will not be shown. - As per P&ID, air inlet filter will be shown before solenoid valve. |  |  | Closed.
11 | Please refer to attached file for air hook-up |  |  | On-off valve as per Airpack standard. Control valve will be updated refer to attached file. |  |  | Filter regulator for on-off valve shall be considered.
12
13