## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 14/Jul./2022 | Rev.:01
|  | Comment Sheet Ref.No.: | Doc Description: UTILITY CONSUMPTION LIST FOR NITROGEN GAS BOOSTER
|  | Transmittal No.: APCES-V-00163 | Doc. No.: BU 20 VD 303 PR LST 0014
|  | Transmittal Date: 14/Jul/2022 | Doc Rev.: 01
Item | CHCE Comment |  |  | Vendor Clarification
1 | 1. Please be noted that the purpose of the utility consumption document is reporting the utilities which consume in a unit. so, for example, instrument air consumption of valve must be reported. |  |  | Noted they have been added CES Reply (Jul.27,2022): Please refer to comments on the document.
2 | Air consumption for control valve, on-off valve and solenoid valve shall be specified. |  |  | Noted they have been added CES Reply (Jul.27,2022): Closed.
3 | .- Please specify workstations power consumption. - Number of required UPS and non-UPS feeders shall be specified as a note. - UPS and non-UPS power consumption shall be reviewed and consumption detail shall be submitted. |  |  | this has been deleted from this document, there is a separate document where this has been incorperated CES Reply (Jul.27,2022): Closed.
4 | EL: Vendor shall add additional information in accordance with attached file. A sample file has been attached into this file. Moreover, other electrical loads shall be added to the above table. |  |  | Noted they have been added CES Reply (Jul.27,2022): Closed. All electrical data shall be shown in separate document (electrical load list).
5
6
7
8
9
10
11
12