## Resolution Sheet
|  |  |  | PROJECT: | 17811
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | P&ID | 17811-03
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 | page 1 | B | Open | This document is checked only for compressor 7080. New document should be generated for compressor 1002. | Noted
2 | Page 5 | B | Open | Compressor design pressure must be mentioned. | Noted and updated
3 | Page 5 | B | Open | 21 | Noted and updated
4 | Page 5 | B | Open | PID No.: BU-20-D-700-PR-PID-711 Line No.: 2"-INA-7001-523C(N) | Noted and updated
5 | Page 5 | B | Open | PAHH | Noted and updated
6 | Page 5 | B | Open | All instrument tag no. procedure in air compressor shall be same as follow: PG-711XX → XX your sequence number | Noted and updated
7 | Page 5 | B | Open | Process properties of shell and tube side must be reported separately. | Noted and updated
8 | Page 5 | B | Open | There are Discrepancies with tags on PID. | Noted and updated |  |  |  | Open
9 | Page 5 | B | Open | Rating shall be specified | Noted and updated |  |  |  | Closed
10 | Page 5 | B | Open | Please modify other instruments transmitter indication and alarm same as mentioned schematic. | Noted and updated
11 | Page 5 | B | Open | PID No.: BU-20-D-700-PR-PID-711 Line No.: 1 1/2"-CWR-7001-500C(N) | Noted and updated
12 | Page 5 | B | Open | 1.5 barg | Noted and updated
13 | Page 5 | B | Open | No.: BU-20-D-700-PR-PID-711 Line No.: 2"-INA-7002-161D(N) | Noted and updated
14 | Page 5 | B | Open | PID No.: BU-20-D-700-PR-PID-711 Line No.: 1 1/2"-CWS-7001-500C(N) | Noted and updated
15 | Page 5 | B | Open | PAHH | Noted and updated
16 | Page 5 | B | Open | Data sheet and PID, must be consistent with each other. According to cooler data sheet cooling water is routed to tube side and air is routed to shell side. | This is purely for drawing purposes only, the datasheet is correct
17 | Page 5 | B | Open | Designation, inlet and out size must be reported. for example 1D1 1/2 | will be updated once PSV calculation is completed
18 | Page 5 | B | Open | Signal shall be specified | Noted and updated
19 | Page 5 | B | Open | Discrepancy with set point & alarm list. In S&A list, unit is Bara. | P&ID is correct and
20 | Page 5 | B | Open | - Tag no. shall be modified. - 2 connection for LG to be considered | Tag no is changed 2 connection LG is not possible this is sight class.
21 | Page 5 | B | Open | pipe to be expanded to 4" for installation of TW on pipe. | Noted and updated
22 | Page 5 | B | Open | Solenoid valve schematic shall be modified to shut down valve and solenoid to be installed on shut down valve (ball type). also signal to solenoid shall be | Noted and updated
23 | Page 5 | B | Open | PSV inlet/outlet size, rating and orifice designation shall be specified. | will be updated once PSV calculation is completed
24 | Page 6 | B | Open | - All instrument tag no. procedure in air compressor shall be same as follow: XY-711XX → XX your sequence number | Noted and updated
25 | Page 6 | B | Open | JB numbering procedure shall be followed same as attached file | Noted and updated
26 | Page 6 | B | Open | UCP-C-7080-01 | Noted and updated
27 | Page 6 | B | Open | Temperature signals shall be specified | Noted and updated
28 | Page 6 | B | Open | Schematic shall be modified for panel mounted | Noted and updated
29 | Page 6 | B | Open | LP-C-7080-01 | Noted and updated
30
31
32
33
34