## Resolution Sheet
PROJECT:
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Wiring diagram | 17811-05B
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 | 1 | 00 |  | Prerequisite document such as I/O list JB wiring diagram shall be issued. | Noted.
2 | 1 | 00 |  | This document is checked only for compressor 7080. New document should be generated for compressor 1002. | This document is for 7080.
3 | 4 | 00 |  | As per MR Supply of PLC(S7 400FH) is in vendor scope of supply as well as Lap top for PLC programing is in vendor scope of supply (for each compressor). Supply of industrial workstation is in vendor scope of supply. | Updated in next revision.
4 | 4 | 00 |  | ? Eex’e’ | Eex’e’ as project specification.
5 | 10 | 00 |  | EL.01: Use circuit breakers to protect the circuit. if a fault occurs after switches, it might upstream C.B to trip and it's not logical. | Circuit breakers are used and also switches for maintenance used.
6 | 10 | 00 |  | redundancy to be considered in panel. | Redundancy is provided.
7 | 10 |  |  | EL02: Incoming power supply terminal numbers shall be clarified. | Note included.
8 | 14 |  |  | To be updated as per comments on Index.(All I/O to be listed in index and this doc will be finalized after receiving of approved index) Tag names to be corrected too. | All this information you can find in the I/O list.
9 | 17 |  |  | dedicated barrier of each AI to be mentioned. | Single channel barriers are used.
10 | 33 |  |  | related signal of each input/output to be mentioned. | all inout/output relays are mentoined in the terminal diagram.
11 | 42 |  |  | All DO signals to be powered by vendor in PLC panel. | Confirmed.
12 | 60 |  |  | EL.03: Refer to comments on page 10. | Noted.
13
14
Open
Closed