## Resolution Sheet
|  |  |  | PROJECT: | 17811
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Calculation and Datasheets of Control valves & on-off valves | 17811-45
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
General | page 1 | 0 | Open | 1. Compressor tag number must be added | Will be incorporated in the next submissin.
1 | page 1 | 0 | Open | 2. Maximum ambient temperature must be considered 52°C | Will be incorporated in the next submissin.
2 | page 1&2 | 0 | Closed | Please add data about only control- / on-off valve. There is no need to submit datasheet of manual valves or check valves. | Please check the manual valve datasheets in this document. We need your comment/approval also on these valves and there is no other suitable document in de VDS.
3 | page 1 | 0 | Open | Data about unloaders valve shall be added to IOM mnual. Please confirm. | Confirmed
4 | page 1 | 0 | Closed | This document is checked only for compressor 7080. New document should be generated for compressor 1002. | Will be incorporated in the next submissin.
5 | page 9 | 0 | Closed | Related solenoid valve data shall be mentioned in this section. | Solenoid valve datasheet are incorporated in the document 17811-12 Instrument datasheets page 30.
6 | page 9 | 0 | Closed | Solenoid valves signals shall be Ex ia | as per TCL point M33 Exd will be used. This has been confirmed
7 | page 10&14 | 0 | Open | Calculations shall be submitted | Will be submitted after purchase. |  |  |  | Open
8 | page 12 | 0 | Closed | Please clarify it is not found. | It is the filter/regulator at the inlet of compressor before the solenoid valve XY-10001. |  |  |  | Closed
9 | page 13&15 | 0 | Closed | Related positioner data shall be mentioned in this section. | Not applicable as PCV has been cancelled
10 | page 13&15 | 0 | Closed | Positioner signals shall be Ex ia | Not applicable as PCV has been cancelled
11 | page 13&15 | 0 | Closed | Valve travel shall be specified | Not applicable as PCV has been cancelled
12 | page 13&15 | 0 | Closed | Noise level shall be specified | Not applicable as PCV has been cancelled
13
14
15
16
17
18
19
20
21
22
23
24
25
26