## Resolution Sheet
PROJECT:
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Load list | 17811-65A
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 | Page 1 | 0 | Open | We required your UCP panel heat dissipation to calculate HVAC capacity for control room, so as per attached sample file heat dissipation shall be specified by AIRPACK in this document. | Noted, however will not be provided in this dodcument, we will provide as soon as the panel components are finalized for information only
2 | Page 1 | 0 | Open | For electrical equipment please modify document as per attached file. | Noted and incorperated
3 | Page 1 | 0 | Open | Oil heater power consumption shall be specified | Noted and incorperated
4 | Page 2 | 0 | Open | According to clause M29 of TCL this shall be 55 kw. | This was a Typo, as the abdorbed power is only 37 kW so 45 is more then sufficient.
5 | Page 2 | 0 | Open | We assumed that OWS power supply will be provided by UCP panel please confirm. | OW power to be done by client
6 | Page 2 | 0 | Open | Following notes shall be added and mentioned in row B1,B2 and C1 - Totally, Two UPS 110VAC feeders (as redundant) and one Non-UPS 230VAC feeder for UCP-C1002-01 will be provided by Owner. - Power distribution for panels, work stations and all related accessories completed by UCP. - Power cable from UCP to OWS will be supplied by AIRPACK.(50m to be considered) | - Noted - No power distibution form UCP - Not considered by Airpack
7 | [8 empty] | Open
8 | [8 empty] | Closed
9
10
11
12
13
14
15
16
17
18
19
20