## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 21/Aug/2020 | Rev.: 00
|  | Comment Sheet Ref.No.: | Doc Description: UCP/LCP/JB GENERAL ARRANGEMENT DRAWING & TERMINAL DETAILS FOR EMERGENCY INSTRUMENT AIR COMPRESSOR INCL. BOM
|  | Transmittal No.: APCES-V-00038 | Doc. No.: BU-20-VD-303-IN-DWG-0089
|  | Transmittal Date: 19/10/2021 | Doc Rev.: 01
Item | CHCE Comment |  |  | Vendor Clarification
1 | dust filter to be added too. |  |  | Updated in next revision
2 | tag plate of each panel/JB to be added too. |  |  | Updated in next revision
3 | grounding of panel to be added too. 3 separate earth bar shall be considered PE, IS-IE, NIS-IE. |  |  | ISE and PE are included in panel
4 | to be in accordance with cable sch |  |  | Updated in next revision
5 | this page to be moved after page |  |  | Updated in next revision
6 | comments on PLC / JBof C-1002 are applicable for C-7080 |  |  | Updated in next revision