## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 20/Oct/2021 | Rev.:00
|  | Comment Sheet Ref.No.: | Doc Description: INSTRUMENT CABLE LIST & SHEDULE FOR EMERGENCY INSTRUMENT AIR COMPRESSOR
|  | Transmittal No.: APCES-V-00039 | Doc. No.: BU-20-VD-303-IN-LST-0088
|  | Transmittal Date: 20/10/2021 | Doc Rev.: 00
Item | CHCE Comment |  |  | Vendor Clarification
1 | Cables numbering procedure, cable type, gland size, number of pair/core and sheath color shall be as per attached file. Numbering of single pair cables is the same as instrument tag numbers. |  |  | For internal cables the numbering procedure will not be followed. Cable tag numbers are according to per wiring diagram.
2 | This document is checked only for compressor 7080. New document should be generated for compressor 1002. |  |  | Noted. It will be incorporated.
3 | cable specification to be added for each cable. ARM./ UNAR SHEATH /color PROTECTION (IS/NIS) CABLE LAYERS … |  |  | Noted. Cable information such as arm/unarm, sheath color, protection and cable type will be added.
4 | cable length to be added for each item except customer scope of supply . |  |  | The cables are internal cables, so the length will not be indicated.
5 | FOR CABLE TAG PLEASE NOTE ATTACHED NUMBERING PROCEDURE. |  |  | For internal cables the numbering procedure will not be followed. Cable tag numbers are according to per wiring diagram.
6 | Gland size to be selected as per attache file. |  |  | Noted. It will be incorporated.
7 | AO signal to be connected to analogue JB |  |  | Noted. It will be incorporated.
8 | signals between MCC and LCP/PLC to be corrected as per project PID. |  |  | Noted. It will be udpated according to per P&ID.