## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 25/Oct/2021 | Rev.:02
|  | Comment Sheet Ref.No.: | Doc Description: Calculation & Datasheet of Control valves / On-off valves for Nitrogen gas booster
|  | Transmittal No.: APCES-V-00041 | Doc. No.: BU-20-VD-303-IN-DSH-0041
|  | Transmittal Date: 25/10/2021 | Doc Rev.: 02
Item | CHCE Comment |  |  | Vendor Clarification
1 | All page of datasheet to be in project title block. |  |  | Format can't be changed for this document, however we will add contracter and client logo in each page.
2 | P&ID number to be modified as per related P&ID document number for all instruments. |  |  | Updated in next revision
3 | Line number of each PSV shall be specified. |  |  | Updated in next revision
4 | To be modified |  |  | Updated in next revision
5 | Ambient |  |  | Updated in next revision
4 | According to PID, solenoid valve as an accessories shall be considered for On-off valve. |  |  | According P&ID Solenoid valves have a seperate TAG-no. Thus considered as a seperate item with corresponding datasheet.
5 | Leakage class shall be specified. |  |  | Updated in next revision
6 | Trim, seat, ball, stem etc.material shall be specified. |  |  | Updated in next revision
7 | Please clarify why 2 pneumatic connection is required. |  |  | This is standrad for pneumatic actuator, for single action 1x will be used, for double acting 2x will be used.
8 | Actuator yoke and housing shall be carbon steel. |  |  | Rack&pinion type actuator do notvhave a yoke and casrbon steel housing is not available. Aluminium epoxy coated is Airpack standard and suitable for this application en evironment.
9 | Recheck |  |  | Updated in next revision
10 | Nitrogen |  |  | Updated in next revision
11
12
13
14
15
16
17
18
19
20
21