## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 27/Oct/2021 | Rev.:01
|  | Comment Sheet Ref.No.: | Doc Description: Calculation & Datasheet of Safety valves for Nitrogen Gas Booster
|  | Transmittal No.: APCES-V-00042 | Doc. No.: BU-20-VD-303-IN-DSH-0015
|  | Transmittal Date: 27/10/2021 | Doc Rev.: 01
Item | CHCE Comment |  |  | Vendor Clarification
1 | All page of datasheet to be in project title block. |  |  | Format can't be changed for this document, however we will add contracter and client logo in each page.
2 | P&ID number to be modified as per related P&ID document number for all instruments. |  |  | Updated in next revision
3 | Line number of each PSV shall be specified. |  |  | Updated in next revision
4 | Required capacity for each PSV shall be specified by Airpack. |  |  | Updated in next revision
5 | Close bonnet type shall be considered for all PSV's |  |  | Updated in next revision
6 | All valves will be furnished with a threaded cap over the spring-adjusting screw |  |  | Updated in next revision
7 | Lifting levers shall be furnished for all safety valves in air service. |  |  | Updated in next revision
8 | Test gags shall be furnished on all safety and relief valves |  |  | Updated in next revision
9 | Body bonnet bolt & nut material shall be specified |  |  | Updated in next revision
10 | PSV's pre calculation shall be submitted by Airpack |  |  | Updated in revision after purchase
11
12
13
14
15
16
17
18
19
20
21