## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 27/Oct/2021 | Rev.:02
|  | Comment Sheet Ref.No.: | Doc Description: Instrument Datasheets for Nitrogen gas booster
|  | Transmittal No.: APCES-V-00042 | Doc. No.: BU-20-VD-303-IN-DSH-0040
|  | Transmittal Date: 27/10/2021 | Doc Rev.: 02
Item | CHCE Comment |  |  | Vendor Clarification
1 | P&ID number to be modified as per related P&ID document number for all instruments. |  |  | Updated in next revision
2 | General comment for all PG/PDG gauges shall be provided with zero stop pin and zero adjustable mechanis, shall be provided. |  |  | Updated in next revision
3 | As per project specification PDG connection shall be 1/2" NPT |  |  | For PDG 1/4" is standard connection, 1/2" not available. Airpack will supply 1/4"/ 1/2" connectors.
4 | 0-25 standard range to be considered |  |  | Updated in next revision
5 | Bar (g) |  |  | All other pressures in process and scales are indicated with bar(a)
4 | Gauges with maximum scale value of 25 bar g and more shall be solid front |  |  | Updated in next revision
5 | Please be informed that pipe to be expanded to 4" for installation of TW on pipe |  |  | Noted, however line number as per P&ID.
6 | Stem orientation shall be every angle. |  |  | This is for fieldmounted gauges, not fpr panel mounted.
7 | 10004/ 10002; based on based on vendor PID |  |  | Not clear what you mean please clarify.
8 | U-length shall be specified by Airpack so that with considering TW tip stai on the middle third of pipe. |  |  | Updated in next revision
9 | XY-71102 is missed |  |  | This tag is not mentioned in the P&ID.
10 | XY-10002 is one of the XV-10002 accessories it shall be removed and mentioned in On-off valve datasheet. |  |  | As it has a separate Tag number a seperated dataheet has been incorporated and not only an accessorie of valves.
11
12
13
14
15
16
17
18
19
20
21