## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 04/Nov/2021 | Rev.: 04
|  | Comment Sheet Ref.No.: | Doc Description: GENERAL ARRANGEMENT DRAWING FOR NITROGEN GAS BOOSTER
|  | Transmittal No.: APCES-V-00046 | Doc. No.: BU-20-VD-303-ME-DWG-0023
|  | Transmittal Date: 04/11/2021 | Doc Rev.: 04
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CHCE Reply | Vendor Clarification
1 | Reply sheet shall be submitted by vendor. |  |  | Noted
2 | Prerequisite document such as wiring diagram and instrument index to be issued before this document |  |  | Doccument supply based on VDS, no order in document submission.
3 | Coordinate of instruments location (X,Y,Z) regarding te base point shall be specified
4 | Cable tray routing shall be specified |  |  | Cable tie-in points are indicated, cable tray routing to juncition boxes is indicated. Internal cable trays will not be included on GA.
5 | Cable tray cross sections shal be specified |  |  | Cable tray cross section will not be indicated on this document, 50x50mm cable trays are used.
6 | North |  |  | Noted and updated
7 | If this is base point please specify in the legend? |  |  | Base point symbol added with discription
8 | This detail not compatible with wire size 16 |  |  | Earth lugg included according comments on Rev-01 of this document and suitable for 70mm² cable.
9 | Earth lug detail for 16 size cable, shall be according attach file, also shall be minimum #2 No. - Galv. Steel plate 12 mm thick. |  |  | Earth lugg updated according comments on Rev-01 of this document. No attachment included in te comments hence earth lug will not be changed.
10 | Please specify anchor box dimensions |  |  | Noted will be included
11 | It is recommended to use type DZ for anchor bolts |  |  | Noted, please revert on Instrument Air Booster package to use similar type for both packages
12 | Bolt dimensions |  |  | "Bolt dimensions will be updated according specification: Thread length is 4xD= 80 (note 2) Projection = 30 + 10 + 80 = 120. Bolt length = 390 = 120 = 510 Please correct is necesarry,"
13 | J |  |  | Detail view indicator for view J.
14 | Instrument tag no. Procedure to be modified as per comment on PID |  |  | Tag-nrs will be updated as per P&ID.
15 | Other instrument based on comment on P&ID shall be added to instrument data |  |  | Table will be updated as per P&ID.
16 | JB tag no. To be modified as per PID and JBs specified in the GA too |  |  | Noted will be udated acc. P&ID
17 | Discrepancy with PID, in PID 2" |  |  | Noted, PID updated to 1½"
18 | 5200 Kg |  |  | Noted will be updated.
19