## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 24/Nov/2021 | Rev.:01
|  | Comment Sheet Ref.No.: | Doc Description: I/O LIST FOR NITROGEN GAS BOOSTER
|  | Transmittal No.: APCES-V-00056 | Doc. No.: BU-20-VD-303-IN-LST-0034
|  | Transmittal Date: 24/Nov/2021 | Doc Rev.: 01
Item | CHCE Comment |  |  | Vendor Clarification
1 | I/O list shall be revised based on comments on P&ID. |  |  | Noted. It will be incorporated.
2 | PB-10003 on local panel, for compressor ESD PB is missed in I/O list. Please clarify about HM-10001 signal, why are you considering a light for hourmeter? what does this light do? |  |  | ESD button on LP will be added. HM is hourmeter, without light. The instrument type will be adjusted.
3 | P&ID number to be modified as per related P&ID document number. |  |  | Noted. It will be incorporated.
4 | (Unload/Stop) |  |  | Noted. It will be incorporated.
5 | To be specified |  |  | Noted. It will be incorporated.
6 | Please modify to "-" |  |  | Noted. It will be incorporated.
7 | State 0 must be Off/Local |  |  | Noted. It will be incorporated.
8 | State 1 must be Remote only |  |  | Noted. It will be incorporated.
9 | Tag no. shall be specified |  |  | Please advise the tag numbers.
10 | XCS-108 |  |  | Noted. It will be incorporated.
11 | FCS |  |  | Noted. It will be incorporated.
12 | HS-108-SD-1 |  |  | Noted. It will be incorporated.
13 | XAL-108-2 |  |  | Noted. It will be incorporated.
14 | XS-115 to be deleted |  |  | Noted. It will be incorporated.