## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 14/12/2021 | Rev.: 02
|  | Comment Sheet Ref.No.: | Doc Description: UCP/LCP/JB GENERAL ARRANGEMENT DRAWING & TERMINAL DETAILS FOR EMERGENCY INSTRUMENT AIR COMPRESSOR INCL. BOM
|  | Transmittal No.: APCES-V-00068 | Doc. No.: BU-20-VD-303-IN-DWG-0089
|  | Transmittal Date: 14/12/2021 | Doc Rev.: 02
Item | CHCE Comment |  |  | Vendor Clarification
1 | dust filter to be added too. |  |  | Updated in next revision CES REPLY: Closed.
2 | tag plate of each panel/JB to be added too. |  |  | Updated in next revision CES REPLY: Closed.
3 | grounding of panel to be added too. 3 separate earth bar shall be considered PE, IS-IE, NIS-IE. |  |  | ISE and PE are included in panel CES REPLY: Please see comments inside document.
4 | + |  |  | Updated in next revision CES REPLY: Closed.
5 | this page to be moved after page |  |  | Updated in next revision CES REPLY: Closed.
6 | comments on PLC / JBof C-1002 are applicable for C-7080 |  |  | Updated in next revision CES REPLY: Closed.
comments revision 01 below
1 | Modify the MC logo |  |  | Format is the same as the P&ID
2 | EL02: 1- The rear of the door shall be shown with mounted devices and wiring channel. 2-The suitable provision shall be considered for separation of 24Vdc and 230VAC in all trunking and ways. |  |  | Rear side can not be shown this is not part of the panel layout Confirmed separation of 24VDC and 230VAC in all trunking and ways
3 | LCP shall be equipped to Ammeter as per TCL |  |  | LCP do not have a Ammeter only on the Distribution panel there is a Ammeter check P&ID
4 | EL-03: The terminal Strip code is specified, but terminal numbers shall be add too. |  |  | Updated in next revision
5 | EL01: The technical specifications shall be completed in nameplate. The below items shall be added in name plate: -The degree of protection panel -The permissible withstanding short circuit current -The total weight of panel -The insulation voltage of panel -Manufacturer date -The panel tag |  |  | Confirmed
6
7
8
9
10
11
12
13
14
15
17
18
19
20
21
22
23
24