## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 19/Jan/2022 | Rev.: 05
|  | Comment Sheet Ref.No.: | Doc Description: GENERAL ARRANGEMENT DRAWING FOR NITROGEN GAS BOOSTER
|  | Transmittal No.: APCES-V-00086 | Doc. No.: BU-20-VD-303-ME-DWG-0023
|  | Transmittal Date: 19/Jan/2022 | Doc Rev.: 05
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CHCE Reply | Vendor Clarification
1 | Reply sheet shall be submitted by vendor. |  |  | Noted |  |  | Noted.
2 | Prerequisite document such as wiring diagram and instrument index to be issued before this document |  |  | Doccument supply based on VDS, no order in document submission. |  |  | Some instruments are specified in this document that is not specified in P&ID and I/O list and instrument list. Please clarify? | New P*ID was submitted, please check again
3 | Coordinate of instruments location (X,Y,Z) regarding te base point shall be specified | [5 empty] | Closed.
4 | Cable tray routing shall be specified |  |  | Cable tie-in points are indicated, cable tray routing to juncition boxes is indicated. Internal cable trays will not be included on GA. |  |  | Noted.
5 | Cable tray cross sections shal be specified |  |  | Cable tray cross section will not be indicated on this document, 50x50mm cable trays are used. |  |  | Noted.
6 | North |  |  | Noted and updated |  |  | Closed.
7 | If this is base point please specify in the legend? |  |  | Base point symbol added with discription |  |  | Noted.
8 | This detail not compatible with wire size 16 |  |  | Earth lugg included according comments on Rev-01 of this document and suitable for 70mm² cable. |  |  | Please see comments inside documents. | Earth lugg updated according comments on Rev-04 of this document. No attachment included in te comments hence earth lug will not be changed.
9 | Earth lug detail for 16 size cable, shall be according attach file, also shall be minimum #2 No. - Galv. Steel plate 12 mm thick. |  |  | Earth lugg updated according comments on Rev-01 of this document. No attachment included in te comments hence earth lug will not be changed. |  |  | Please see comments inside documents. | Earth lugg updated according comments on Rev-04 of this document. No attachment included in te comments hence earth lug will not be changed.
10 | Please specify anchor box dimensions |  |  | Noted will be included |  |  | Closed.
11 | It is recommended to use type DZ for anchor bolts |  |  | Noted, please revert on Instrument Air Booster package to use similar type for both packages |  |  | Closed.
12 | Bolt dimensions |  |  | "Bolt dimensions will be updated according specification: Thread length is 4xD= 80 (note 2) Projection = 30 + 10 + 80 = 120. Bolt length = 390 = 120 = 510 Please correct is necesarry," |  |  | Closed.
13 | J |  |  | Detail view indicator for view J. |  |  | Closed.
14 | Instrument tag no. Procedure to be modified as per comment on PID |  |  | Tag-nrs will be updated as per P&ID. |  |  | Noted.
15 | Other instrument based on comment on P&ID shall be added to instrument data |  |  | Table will be updated as per P&ID. |  |  | P&ID must be issued before this document. | Noted
16 | JB tag no. To be modified as per PID and JBs specified in the GA too |  |  | Noted will be udated acc. P&ID |  |  | Noted.
17 | Discrepancy with PID, in PID 2" |  |  | Noted, PID updated to 1½" |  |  | Closed.
18 | 5200 Kg |  |  | Noted will be updated. |  |  | Closed.
19
20 | This detail not compatible with wire size 16 |  |  | Upto now your reference drawing was not received
21 | Earth lug detail for 16 size cable, shall be according attach file, also shall be: -minimum #2 No. -GALV. steel plate 12mm THICK |  |  | Upto now your reference drawing was not received
22 | Nitrogen Gas Booster Comp. |  |  | Noted will be updated.
23 | None of the tag numbers is found in PID. New revision of P&ID shall be submitted before issuing next revision of GA drawing. |  |  | Noted have been updated according to new P&ID
24 | Discrepancy with PID. in PID 2" |  |  | Noted will be updated.
25 | Important comment: Any wires carrying an AC signal of 400V are a possible source of electromagnetic interference, and instrument signal cables and JBs shall be installed a safe distance from them. Please modify JB and cable tray arrangement accordingly (Need to be discussed in meeting, if necessary) |  |  | This is taken into account
26 | - Some tags have been added that is not in nitrogen P&ID rev. 01, so this document can not be checked till P&ID and wiring diagram issued. - XV-10152 to be specified. |  |  | Noted have been updated according to new P&ID
27 | Personal protection for line with temperature above 60C is in airpack scope. |  |  | Noted This will be taken into account
28
29
30
31
32