## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 03/Feb/2022 | Rev.:04
|  | Comment Sheet Ref.No.: | Doc Description: Instrument Datasheets for Nitrogen gas booster
|  | Transmittal No.: APCES-V-00091 | Doc. No.: BU-20-VD-303-IN-DSH-0040
|  | Transmittal Date: 03/Feb/2022 | Doc Rev.: 04
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply | Vendor Clarification (2) | CES Reply (2)
1 | P&ID number to be modified as per related P&ID document number for all instruments. |  |  | Updated in next revision |  |  | Closed.
2 | General comment for all PG/PDG gauges shall be provided with zero stop pin and zero adjustable mechanis, shall be provided. |  |  | Updated in next revision |  |  | Closed.
3 | As per project specification PDG connection shall be 1/2" NPT |  |  | For PDG 1/4" is standard connection, 1/2" not available. Airpack will supply 1/4"/ 1/2" connectors. |  |  | Closed.
4 | 0-25 standard range to be considered |  |  | Updated in next revision |  |  | Closed.
5 | Bar (g) |  |  | All other pressures in process and scales are indicated with bar(a) |  |  | Closed.
4 | Gauges with maximum scale value of 25 bar g and more shall be solid front |  |  | Updated in next revision |  |  | Closed.
5 | Please be informed that pipe to be expanded to 4" for installation of TW on pipe |  |  | Noted, however line number as per P&ID. |  |  | Closed.
6 | Stem orientation shall be every angle. |  |  | This is for fieldmounted gauges, not fpr panel mounted. |  |  | Closed.
7 | 10004/ 10002; based on based on vendor PID |  |  | Not clear what you mean please clarify. |  |  | Closed.
8 | U-length shall be specified by Airpack so that with considering TW tip stai on the middle third of pipe. |  |  | Updated in next revision |  |  | Please specify TW nozzle projection. it seems that selected U-length is too short to TW tip stay on the middle third of pipe. | It is double checked and we confim TW-tip stay on th middel third of pipe. | Closed. It is in vendor responsibility to supply suficant TW length based on project requirements.
9 | XY-71102 is missed |  |  | This tag is not mentioned in the P&ID. |  |  | Closed.
10 | XY-10002 is one of the XV-10002 accessories it shall be removed and mentioned in On-off valve datasheet. |  |  | As it has a separate Tag number a seperated dataheet has been incorporated and not only an accessorie of valves. |  |  | Solenoid valve shall has a separate tag no. but it is one of the XV-10002 accessories and must be mentioned in on-off valve data sheet and removed from this data sheet. | Cross reference will be made on the XV-10002 datasheet referinge to the XY-10002 datasheet | Closed.
11 | - Please issue this document after P&ID approval and received sub-vendor complete information. |  |  | P&ID has been updated, inquiries for instruments are sent after approval of drawings, only af that the fnal information will be submitted. So please first approve the items as they are now so we can sent inquiries to our sub-vendors. |  |  | Updated P&ID has not been issued yet, latest revision of P&ID (rev.1) has not conformity with instrument data sheet. Noted, instrument MFR and model must be specified after data sheet approval. | P&ID rev.02 has been issued 3/11/2021. | Closed.
12 | - Manufacturer and Model no. for all items must be specified. |  |  | see reply Item 11 |  |  | See reply Item 11 |  | Specifying MFR. and model no is not related to P&ID, regarding to data sheet was approved as note you must specify mentioned items.
13 | - All "VTA" and "To be advised by supplier" and etc. to be specified in next rev. |  |  | see reply Item 11 |  |  | See reply Item 11 |  | See reply item 12.
14 | Document shall be updated based on comments on P&ID |  |  | Updated in next revision |  |  | Closed.
15 | 85 oC.the comment is valid for other instruments on the line. |  |  | Updated in next revision |  |  | Closed.
16 | Based on PID the operating temperature of the inter cooler is 180 oC while the normal and Max. temperature of the relevant instruments do not cover it. This comment is valid for other related document such as PSV Data Sheet. |  |  | 180° C is not mentioned on the PID |  |  |  | O.T is 134°C as per P&ID | Closed.
17 | 100 oC.Must be consider for all cooling water lines |  |  | 95°C as per PID will be updated in next revision. |  |  | Not accepted. The comment must be taken into consideration. | D.T is 95°C as per P&ID | Closed.
18 | 7 barg. Must be consider for all cooling water lines. |  |  | 10 barg as per PID will be updated in next revision. |  |  | Not accepted. The comment must be taken into consideration. | D.P is 10 barg as per P&ID | Closed.
19
19 | G.N 1. Any nodification must be highlighted. |  |  | Modifications highlighted in red. |  |  |  |  | Closed.
20 | G.N 2. All documents must be consistent with each other in terms of tag.numbers, line numbers and so on. |  |  | Updated in next revision |  |  |  |  | Closed.
21 | G.N 3. It is not clear why tag numbers are being changed, yet this document will be finalized when PID is issued. |  |  | Tagnumbers as per P&ID. |  |  |  |  | Closed.
22 | PG-10161 |  |  | Updated in next revision |  |  |  |  | Closed.
23 | Gauge savers shall be considered for the services such that full scale of the gauge is smaller than its design pressure. |  |  | Full scale range will be updated in next revision. |  |  |  |  | Closed.
24 | Repeated comment; Airpack shall submit Wake Frequency calculation sheets to meet ASME PTC 19.3 to purchaser for approval. |  |  | Calculations are not part of the agreed scope of supply. |  |  |  |  | According to signed MRQ by Airpack, section RFD, page 26, clause TE97 "Stress analysis and Calculation for thermowell" shall be supplied by Airpack.(your temp. element sub-vendor must submit wake frequency calculation)
25
25 | Manufacturer and model no. must be specified after data sheet approval or approved as note. also "VTA" , "To be advised by supplier" and etc. must be specified too. |  |  | Updated in next revision "AFC" after purchase.
25 | Repeated comment; Airpack shall submit Wake Frequency calculation sheets to meet ASME PTC 19.3 to purchaser for approval. |  |  | According to signed MRQ by Airpack, section RFD, page 26, clause TE97 "Stress analysis and Calculation for thermowell" shall be supplied by Airpack.(your temp. element sub-vendor must submit wake frequency calculation), however it is only mentioned if applicable, and it is not menioned in the specifcation if it is applicable. therefore it has not been considered
25