## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 03/Feb/2022 | Rev.:04
|  | Comment Sheet Ref.No.: | Doc Description: Instrument Datasheets for Emergency Instrument air compressor
|  | Transmittal No.: APCES-V-00091 | Doc. No.: BU-20-VD-303-IN-DSH-0090
|  | Transmittal Date: 03/Feb/2022 | Doc Rev.: 04
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply | Vendor Clarification (2) | CES Reply (2)
1 | P&ID number to be modified as per related P&ID document number for all instruments. |  |  | Updated in next revision |  |  | Closed.
2 | General comment for all PG/PDG gauges shall be provided with zero stop pin and zero adjustable mechanis, shall be provided. |  |  | Updated in next revision |  |  | Closed.
3 | Ambient / 45°C |  |  | Updated in next revision |  |  | Closed.
4 | As per project specification PDG connection shall be 1/2" NPT |  |  | For PDG 1/4" is standard connection, 1/2" not available. Airpack will supply 1/4"/ 1/2" connectors. |  |  | Closed.
5 | Instrument Air |  |  | Updated in next revision |  |  | Closed.
6 | 0-40 standard range to be considered |  |  | Updated in next revision |  |  | Closed.
7 | Bar (g) |  |  | All other pressures in process and scales are indicated with bar(a) |  |  | Closed.
8 | Gauges with maximum scale value of 25 bar g and more shall be solid front |  |  | Updated in next revision |  |  | Closed.
9 | Please be informed that pipe to be expanded to 4" for installation of TW on pipe |  |  | Noted, however line number as per P&ID. |  |  | Closed.
10 | Stem orientation shall be every angle. |  |  | This is for fieldmounted gauges, not fpr panel mounted. |  |  | Closed.
11 | 10004/ 10002; based on based on vendor PID |  |  | Not clear what you mean please clarify. |  |  | There is no such a comment | Noted
12 | U-length shall be specified by Airpack so that with considering TW tip stai on the middle third of pipe. |  |  | Updated in next revision |  |  | Please specify TW nozzle projection. it seems that selected U-length is too short to TW tip stay on the middle third of pipe. | It is double checked and we confim TW-tip stay on th middel third of pipe. | Closed. It is in vendor responsibility to supply suficant TW length based on project requirements.
13 | Airpack shall submit wake frequency calculations sheets to meet ASME PTC 19.3 to purchaser for approval. |  |  | This has not been agreed upon in the contract. |  |  | Please attach related MOM or TCL about this agreement. | Please mention where this is mentioned in the specification | According to signed MRQ by Airpack, section RFD, page 26, clause TE97 "Stress analysis and Calculation for thermowell" shall be supplied by Airpack.(your temp. element sub-vendor must submit wake frequency calculation)
14 | XY-10002 is one of the XV-10002 accessories it shall be removed and mentioned in On-off valve datasheet. |  |  | As it has a separate Tag number a seperated dataheet has been incorporated and not only an accessorie of valves. |  |  | Solenoid valve shall has a separate tag no. but it is one of the XV-71102 accessories and must be mentioned in on-off valve data sheet and removed from this data sheet. | Cross reference will be made on the XV-10002 datasheet referinge to the XY-10002 datasheet | Closed.
15 | - Please issue this document after P&ID approval and received sub-vendor complete information. |  |  | P&ID has been updated, inquiries for instruments are sent after approval of drawings, only af that the fnal information will be submitted. So please first approve the items as they are now so we can sent inquiries to our sub-vendors. |  |  | Noted, instrument MFR and model must be specified after data sheet approval. | noted | Comment was not implemented.
16 | - Manufacturer and Model no. for all items must be specified. |  |  | see reply Item 11 |  |  | See reply Item 11 |  | Comment was not implemented.
17 | - All "VTA" and "To be advised by supplier" and etc. to be specified in next rev. |  |  | see reply Item 11 |  |  | See reply Item 11 |  | Comment was not implemented.
19 | 85 oC.the comment is valid for other instruments on the line. |  |  | Updated in next revision |  |  | Closed.
21 | 100 oC.Must be consider for all cooling water lines |  |  | 95°C as per PID will be updated in next revision. |  |  | Not accepted. The comment must be taken unto consideration. | D.T is 95°C as per P&ID | PR Reply: Closed
22 | 7 barg. Must be consider for all cooling water lines. |  |  | 10 barg as per PID will be updated in next revision. |  |  | Not accepted. The comment must be taken unto consideration. | D.P is 10 barg as per P&ID | PR Reply: Closed
23
23 | Current revision is REV.02 |  |  | Updated in next revision |  |  |  |  | Closed.
24 | in PTD OT (shell is reported 180°C |  |  | Updated in next revision |  |  |  |  | Closed.
24 | Based on Basis of design of the project design temperature must be specified by the following rule: |  |  | D.T updated are as per P&ID. |  |  |  |  | Closed.
| Design temperature for PROCESS equipment shall whichever is higher: | [7 empty] | Closed.
| • maximum operating temperature +15°C (+25°C for Feed/Effluent exchanger) | [7 empty] | Closed.
| • boiling temperature at design pressure of PROCESS medium inside, if applicable | [7 empty] | Closed.
| Design temperature shall be rounded up to full 5°C steps | [7 empty] | Closed.
| Design minimum temperature shall be specified only if the minimum operating temperature is below 0°C. Design minimum temperature shall be 5°C less than the minimum operating temperature. Special attention shall be given to low boiling liquids such as LPG. | [7 empty] | Closed.
| For piping, design temperature shall be determined according to ASME B31.3. | [7 empty] | Closed.
| The comment is valid for all instruments . | [7 empty] | Closed.
25 | Based on Basis of design of the project design pressure must be specified by the following rule: |  |  | D.P are as per P&ID. |  |  |  |  | Closed.
| Design pressure of process static EQUIPMENT shall be based on the max. operating pressure. | [7 empty] | Closed.
| Malfunction and EQUIPMENT failure shall be taken into consideration by safety devices. | [7 empty] | Closed.
| Design pressure shall be selected from the list below: | [7 empty] | Closed.
| • for max operating pressure below 2 barg use 3.5 barg | [7 empty] | Closed.
| • for max operating pressure between 2 barg and 15 barg use max operating pressure +1.5 bar | [7 empty] | Closed.
| • for max operating pressure between 15 barg and 100 barg use max operating pressure x 110% | [7 empty] | Closed.
| • for max operating pressure equal and above 100 barg use max operating pressure +10 bar | [7 empty] | Closed.
| The comment is valid for all instruments. | [7 empty] | Closed.
26 | Gauge savers shall be considered for the services such that full scale of the gauge is smaller than its design pressure. |  |  | Full scale range will be updated in next revision. |  |  |  |  | Closed.
27 | Repeated comment; Airpack shall submit Wake Frequency calculation sheets to meet ASME PTC 19.3 to purchaser for approval. |  |  | Calculations are not part of the agreed scope of supply. |  |  |  |  | According to signed MRQ by Airpack, section RFD, page 26, clause TE97 "Stress analysis and Calculation for thermowell" shall be supplied by Airpack.(your temp. element sub-vendor must submit wake frequency calculation)
28
28 | Manufacturer and model no. must be specified after data sheet approval or approved as note. also "VTA" , "To be advised by supplier" and etc. must be specified too. |  |  | Updated in next revision "AFC" after purchase.
29 | Data sheet and calculation sheet for FO-71101 and FO-71102 that recently added in P&ID shall be bring in this document. (please refer to attached file for sample format of FO data sheet) |  |  | first of all no sample format was received, secondly this is calculation from API 618 approach 2, so the information regarding the FO can be found there and will not be added to this datasheet
30 |  |  |  | Design pressures are as per design pressures on the P&ID, as there were no comments on the P&ID, the same design pressure will be followed.
31 | Repeated comment; Airpack shall submit Wake Frequency calculation sheets to meet ASME PTC 19.3 to purchaser for approval. |  |  | According to signed MRQ by Airpack, section RFD, page 26, clause TE97 "Stress analysis and Calculation for thermowell" shall be supplied by Airpack.(your temp. element sub-vendor must submit wake frequency calculation), however it is only mentioned if applicable, and it is not menioned in the specifcation if it is applicable. therefore it has not been considered
32