## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 14/Feb/2022 | Rev.:02
|  | Comment Sheet Ref.No.: | Doc Description: INSTRUMENT HOOK UP DRAWING FOR NITROGEN GAS BOOSTER
|  | Transmittal No.: APCES-V-00096 | Doc. No.: BU-20-VD-303-IN-DWG-0033
|  | Transmittal Date: 14/Feb/2022 | Doc Rev.: 02
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply | Vendor Clarification (2)
1 | this part is as internal part of valve and 1 integrated on / off valve including ball valve and related SOV will be supplied by vendor. But related instrument air tubing to be indicated in hook up from main header of inst air. |  |  | Intrument air air tubing is already shown. But from main header will be shown as "FROM COM. INLET". |  |  | Required connections to be specified in hook-up. | Noted.
2 | Related instrument air tubing to be indicated in hook up from main header of inst air. |  |  | Intrument air air tubing is already shown. But from main header will be shown as "FROM COM. INLET". |  |  | Please refer to attached file about air hook-up in the document. | Noted.
3 | 2 |  |  | Noted. It will be incorporated.
4 | 8 |  |  | Noted. It will be incorporated.
5 | Length to be specified |  |  | The tubing length is according to the actual engineering. It will not be shown.
6 | - Line service shall be specified.(liquid, gas, etc.) - Nozzle tap orientation shall be same as attached file, and specified in pressure hook-up pages. |  |  | - Noted. The line service will be specified. - The hookup drawing is as per Airpack standard. Nozzle tap orientation will not be shown.
7 | 1 |  |  | Noted. It will be incorporated.
8 | 6 |  |  | Noted. It will be incorporated.
9 | Tube and cap to be considered for drain /vent of manifold. |  |  | Noted. It will be incorporated.
10 | - Air header and required connection to be specified. - Vendor to clarify, whether filter/regulator is required before solenoid valve. |  |  | - This is the compressor inlet solenoid valve on the instrument airline. Airheader will not be shown. - As per P&ID, air inlet filter will be shown before solenoid valve.
11 | Please refer to attached file for air hook-up |  |  | On-off valve as per Airpack standard. Control valve will be updated refer to attached file.
12
13