## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 23/Feb/2022 | Rev.:03
|  | Comment Sheet Ref.No.: | Doc Description: PIPING LINE LITS NITROGEN GAS BOOSTER
|  | Transmittal No.: APCES-V-00100 | Doc. No.: BU-20-VD-303-PR-LST-0065
|  | Transmittal Date: 23/Feb/2022 | Doc Rev.: 03
Item | CHCE Comment |  |  | Vendor Clarification
1 | Considering the fact that C-7080 and C-1002 are two different packages, each of them must have its own line list. |  |  | Added
2 | The class line must be changed to 500C in PID |  |  | Piping line list is updated
3 | Discrepancy. in PID 2" |  |  | Piping line list is updated
4 | Discrepancy. in PID 1.5barg |  |  | Piping line list is updated
5 | 1- Design temperature of cooling water line must be considered 100 oC. 2- for other lines with operating temperature Between - 29 ºC and +60 ºC , the maximum design temperature must be considered 85 oC 3-All changes from previous revision must be highlighted. |  |  | 1- Piping line list is updated 2- Piping line list is updated 3- Updated
6 | Tie-in No. must be added in PID |  |  | added
7 | Following lines must be added: 2"-INA-7001-PR-511C(N) 2"-INA-7002-539D(N) |  |  | These lines were not found in the P&ID.
8 | THIS DOCUMENT SHALL BE IN CONJUNCTION WITH PID WHILE PIPING LINE CLASSES ARE NOT SAME AS LATEST PID FOR BOTH OF COMPRESSORS |  |  | Updated
9
10