## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 08/Mar/2022 | Rev.:03
|  | Comment Sheet Ref.No.: | Doc Description: I/O LIST FOR NITROGEN GAS BOOSTER
|  | Transmittal No.: APCES-V-0109 | Doc. No.: BU-20-VD-303-IN-LST-0034
|  | Transmittal Date: 08/Mar/2022 | Doc Rev.: 03
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply
1 | I/O list shall be revised based on comments on P&ID. |  |  | Noted. It will be incorporated. |  |  | Noted.
2 | PB-10003 on local panel, for compressor ESD PB is missed in I/O list. Please clarify about HM-10001 signal, why are you considering a light for hourmeter? what does this light do? |  |  | ESD button on LP will be added. HM is hourmeter, without light. The instrument type will be adjusted. |  |  | Noted.
3 | P&ID number to be modified as per related P&ID document number. |  |  | Noted. It will be incorporated. |  |  | Noted.
4 | (Unload/Stop) |  |  | Noted. It will be incorporated. |  |  | Noted.
5 | To be specified |  |  | Noted. It will be incorporated. |  |  | Noted.
6 | Please modify to "-" |  |  | Noted. It will be incorporated. |  |  | Noted.
7 | State 0 must be Off/Local |  |  | Noted. It will be incorporated. |  |  | Noted.
8 | State 1 must be Remote only |  |  | Noted. It will be incorporated. |  |  | Noted.
9 | Tag no. shall be specified |  |  | Please advise the tag numbers. |  |  | Please see in the document.
10 | XCS-108 |  |  | Noted. It will be incorporated. |  |  | Noted.
11 | FCS |  |  | Noted. It will be incorporated. |  |  | Noted.
12 | HS-108-SD-1 |  |  | Noted. It will be incorporated. |  |  | Noted.
13 | XAL-108-2 |  |  | Noted. It will be incorporated. |  |  | Noted.
14 | XS-115 to be deleted |  |  | Noted. It will be incorporated. |  |  | Noted.
15 | - Signal for PY-10151 is missed - Please add I/O summary table for each I/O type |  |  | Noted. It will be incorporated. |  |  | Closed.
16 | Please fill xx as your sequence HS-101xx-R HS-101xx-SD XS-101xx-ST/SP XS-101xx-ST/SP XL-101xx YAL-101xx XL-101xx YAL-101xx |  |  | Noted. It will be incorporated. |  |  | Closed.
17 | State must be specified |  |  | Noted. It will be incorporated. |  |  | Please refer to document.
| .- AO signal type shall be added. - I/O redundancy shall be mentioned. |  |  | AO signals is through PID controller I/O reduncacy is mentioned already |  |  | - AO card for control valve must be considered, PID controller is not accepted. - Closed.
| 13 |  |  | Noted. It will be incorporated. |  |  | Closed.
| 16 |  |  | 17 as per wiring diagram |  |  | Please refer to comment on document.
| emergency stop / normal |  |  | Noted. It will be incorporated. |  |  | Closed.
| YAL-10127 |  |  | Noted. It will be incorporated. |  |  | Closed.
| According to existing PLC in your UCP, so PID controller is not accepted and AO card must be considered, and also PID controller has conflict with issued P&ID, in the P&ID, control valve has been controlled via UCP. Please consider one analogue output card to control control valve, with considering related pressure signal that coming to UCP. |  |  | Current wiring diagram and P&ID is with PID controller, which is located in the UCP. It will be activated by the DO on the PLC, pressure signal is transferred internally in the UCP to PID controller. Configuration will not be changed as this is our standard configuration for operating these valves |  |  | It is unusual to consider PID controller while existing PLC/UCP and it cause to decrease system reliability, So as per routine design for control valves in this project and also in other packages analogue output card (AO) shall be considered instead of PID controller for controlling the control valve. Please clarify about your reply "It will be activated by the DO on the PLC" , vendors description is not clear Airpack Reply: there is nothing unusual about this, the PID controller is much more reliable in terms of operatability of the valve. This is our standard configuration for PID controllers. the DO wil activated the PID controlled, like start and stop of the controller. Therefore we will keep it the same as it is now.
| Please refer to comment in previous page |  |  | Current wiring diagram and P&ID is with PID controller, which is located in the UCP. It will be activated by the DO on the PLC, pressure signal is transferred internally in the UCP to PID controller. Configuration will not be changed as this is our standard configuration for operating these valves
| Please clarify? |  |  | Current wiring diagram and P&ID is with PID controller, which is located in the UCP. It will be activated by the DO on the PLC, pressure signal is transferred internally in the UCP to PID controller. Configuration will not be changed as this is our standard configuration for operating these valves