## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 18/Mar/2022 | Rev.:03
|  | Comment Sheet Ref.No.: | Doc Description: LOGIC DIAGRAMS-PROGRAM OF UCP - COMPRESSOR SHUTDOWN LOGIC DRAWING FOR EMERGENCY INSTRUMENT AIR COMPRESSOR
|  | Transmittal No.: APCES-V-00113 | Doc. No.: BU-20-VD-303-IN-DIG-0085
|  | Transmittal Date: 18/Mar/2022 | Doc Rev.: 03
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply
1 | Drawing shall be match the title of the project block |  |  | Noted. It will be incorporated. |  |  | Closed.
2 | Prerequisite document such as cause & effect, control philosophy and I/O list shall be issued. |  |  | Noted. It will be incorporated. |  |  | Closed.
3 | This document is checked only for compressor 7080. New document should be generated for compressor 1002. |  |  | The documents will be separately made for each compressor. |  |  | Closed.
4 | tag names to be updated based on PID. All loops to be added to logic (FT/PCV/VT...) |  |  | Noted. It will be incorporated. |  |  | Closed.
5 | to be updated based on PID |  |  | Noted. It will be incorporated. |  |  | Closed.
6 | EL.01: It's not clear. one Emergency push button there is on LCP in accordance with standard drawings and philosophy. |  |  | This is stop button, not emergency shutdown button. For ESD pushbutton, please refer to Sheet 2. |  |  | This comment is not related to logic.
| - Following items are missed, please consider in logic : • HS-715-SD-1 Emergency Shutdown Command from ESD System • XAL-715-2 Common Alarm to ESD System • XS-715 Interlock Switch Stop Compressor from FCS • Heater |  |  | 1) The HS-715-SD-1 goes straight to the ESD relay. Furthermore, there is no need to be shown in the logic once the logic monitors the output signal of the ESD relay. 2)Noted. It will be incorporated. 3)Noted.It will be incorporated. 4)The Oil Heater works stand-alone without connection with the PLC. So there is no influence on the logic diagram. For further information, please check the wiring diagram. |  |  | 1) Using Emergency shutdown relay is not accepted. Same as ESD PBs on UCP and LCP that connected to the I/O cards, HS-715-SD-1 Emergency Shutdown Command from ESD System shall be connected to I/O card and effected in logic. 2) XAL-715-2 is not common alarm, it is trip status to ESD system, so logic shall be modify accordingly. 3) Noted. 4) Please clarify about On/Off command, Fault and Running status of oil heater in I/O list.(it seems that oil heater controlled by UCP)
| Repeated Comment - Following items are missed, please consider in logic : • HS-715-SD-1 Emergency Shutdown Command from ESD System • XAL-715-2 Shutdown status to ESD System • Heater |  |  | The command HS-715-SD-1 goes directly to the ESD Relay. The Heater is controlled by hardware, for further information check the wiring diagram.
| Any changes shall be specified with revision mark and revision cloud. |  |  | Noted
| Logic for XAL-715-2 is not true this signal sent shutdown status to client ESD system. |  |  | According to the wiring this signal is the common alarm to DCS.