## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 17/May/2022 | Rev.:02
|  | Comment Sheet Ref.No.: | Doc Description: INSTRUMENT HOOK UP DRAWING FOR EMERGENCY INSTRUMENT AIR COMPRESSOR
|  | Transmittal No.: APCES-V-00135 | Doc. No.: BU-20-VD-303-IN-DWG-0103
|  | Transmittal Date: 17/May/2022 | Doc Rev.: 02
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply | Vendor Clarification (2)
1 | - Please refer to comments on Hook-up Drawing For Nitrogen Compressor "BU-20-VD-303-IN-DWG-0033-01" |  |  | Noted. |  |  | Please refer to comments on document | Noted.
| In gas services, pressure tapping shall be in 12 o'clock of pipe, also tapping orientation shall be specified in pressure hook-up with figure or as a note. |  |  | Noted. It will be incorporated. |  |  | Closed.
| Pressure hook-up for gas and liquid services shall be segregated and specified in different pages, because of in gas services, pressure tapping shall be in 12 o'clock of pipe and in liquid services, pressure tapping shall be in 6 o'clock of pipe, also tapping orientation shall be specified in pressure hook-up with figure or as a note. |  |  | Noted. It will be incorporated. For the oil pressure transmitter of oil system, the nozzle tapping is not applicable. |  |  | Closed, specified orientation for liquid pressure transmitter was accepted.
| Filter/Regulator |  |  | Noted. It will be incorporated. |  |  | Closed.
| Filter/Regulator shall be added before solenoid valve |  |  | Noted. It will be incorporated. |  |  | Closed.
| Liquid |  |  | Noted. It will be incorporated. |  |  | Closed.
| Tapping orientation shall be specified |  |  | Updated
| 6 |  |  | Updated