## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 03/Jun/2022 | Rev.:02
|  | Comment Sheet Ref.No.: | Doc Description: INSTRUMENT INDEX FOR EMERGENCY INSTRUMENT AIR COMPRESSOR
|  | Transmittal No.: APCES-V-00142 | Doc. No.: BU-20-VD-303-IN-INX-0083
|  | Transmittal Date: 03/Jun/2022 | Doc Rev.: 02
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CHCE Reply | Vendor Clarification(2) | CHCE Reply
1 | As I/O list did not supplied by vendor so all required items in I/o list to be added to index. -Signal Type (4-20mAmp, 24vdc , ...) -From/ To And also all signals to be indicated in this doc (limit switch of valves , remote start stop command (refer to page 4&6 OF pid) |  |  | Noted. Additional I/O information will be added to the existing instruments, and signals to/from ESD/FCS/DB will be added as per P&ID. |  |  | Noted |  | Closed.
2 | This document is checked only for compressor 7080. New document should be generated for compressor 1002. |  |  | New documents will be one instrument index for compressor 1002, and one for compressor 7080. |  |  | Noted |  | Closed.
3 | As per project spec redundancy to be considered where required (for example closed loops) |  |  | Noted. Redundant I/O will be indicated. |  |  | Redundancy is not specified, please modify. | Redundancy is specified underneath I/O TYPE column. | Closed.
4 | To be corrected |  |  | Noted, it will be updated |  |  | PID, Data sheet, wiring and Hook-up document number shall be modified as per VPIS. | Noted. It will be incorporated. | Closed.
5 | There is a deviation between this doc and PID in sequence of tag numbers, please clarify? |  |  | The tag numbers will be updated according to per P&ID. |  |  | Please refer to comment on nitrogen PID for instrument numbering procedure. | Tag numbers are as per P&ID. | Closed.
6 | To be filled carefully,there is not any signal for local gauges. |  |  | Noted. The signals for local gauges will be removed. |  |  | Noted |  | Closed.
7 | Refer to comments on data sheet |  |  | Noted. It will be udpated according to per data sheet. |  |  | Noted |  | Closed.
8 | isolation valve for LG to be considered |  |  | As per P&ID, there's no isolation valve for LG. |  |  | Noted |  | Closed.
9 | For on/off valve DO signals will be considered for solenoid valve not ball valves |  |  | Noted, it will be updated |  |  | Noted |  | Closed.
10 | following items to be added to index: VT FT |  |  | Noted, it will be incorporated |  |  | Noted |  | Closed.
11 | Same as comment on C-1002 |  |  | Noted |  |  | Noted |  | Closed.
12 | *Reply sheet shall be submitted by vendor *Please refer to comment in PID for instrument numbering procedure *PID, data sheet, wiring and hook-up document number shall be modified as per VPIS *This document will be finalized after PID and data sheet approval and considered all comments *PSV-1001 shall be added to teh instrument list *Manufacturer adn model no. to be specified in this document |  |  | Noted |  |  | These comments are related to the nitrogen compressor, |  | Noted, please revise this document after specify mentioned items from your sub-vendor.
13 | Abbreviation to be specified. Please clarify about "DB" |  |  | Distribution board |  |  | Noted. |  | Closed.
14 | Tag number to be specified |  |  | Please advise |  |  | Please refer to numbering procedure and PID legend. | Please specify the tag number which is not specified, such as motor/heater running, fault, start/stop, on/off. | Please refer to I/O List and revised accordingly
15 | Please select as per standard range |  |  | It's according to instrument data sheet |  |  | Range 0~35 shall be modified as per standard range of pressure gauge in this document and data sheet too. | As per instrment datasheet, the range of this pressure gauge will be 1…40 bar(a). | Closed.
16 | Process connection 1/2" NPT-F |  |  | It's according to instrument data sheet |  |  | Noted. |  | Closed.
17 | Manufacturer and model no. shall be specified in next revision. |  |  | They will be specified after placing the order. |  |  | Noted, please revise this document after specify mentioned items from your sub-vendor.
18 | PV-71101 and PY-71101 are missed. |  |  | Noted. They will be added. |  |  | Closed.
19 | To be specified |  |  | It will be specified after placing the order. |  |  | Noted, please revise this document after specify mentioned items from your sub-vendor.
20 | XS-715 Interlock Switch Stop Compressor shall be specified same as previous revision. |  |  | Noted. It will be added. |  |  | Closed.
21 | Tag number to be specified |  |  | Please advise/specify these tag numbers. |  |  | Please refer to I/O List and revised accordingly
| Manufacturer and model no. shall be specified in next revision. |  |  | Updated
| All "TBA", "to be advised", "will be stated later" and ect. items shall be specified. |  |  | Updated
| Following tags has been missed • FO-71101 • FO-71102 |  |  | Updated
| Tag number to be specified. (according to I/O List) |  |  | Updated
| Range to be modified as per data sheet. |  |  | Updated
| IS/NIS for all signals shall be specified. |  |  | Updated
| Discrepancy with PID. In PID 1/2" |  |  | Updated
| Discrepancy with P&ID in valve size please clarify |  |  | Valve size has been clarified
| Discrepancy with PID. In PID 11/2" |  |  | Updated
| PSV inlet/outlet size shall be specified |  |  | Updated.