## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 16/06/2022 | Rev.: 02
|  | Comment Sheet Ref.No.: | Doc Description: UCP/LCP/JB GENERAL ARRANGEMENT DRAWING & TERMINAL DETAILS FOR EMERGENCY INSTRUMENT AIR COMPRESSOR INCL. BOM
|  | Transmittal No.: APCES-V-00149 | Doc. No.: BU-20-VD-303-IN-DWG-0089
|  | Transmittal Date: 156/06/2022 | Doc Rev.: 02
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply
1 | dust filter to be added too. |  |  | Updated in next revision CES REPLY: Closed. |  |  | Closed.
2 | tag plate of each panel/JB to be added too. |  |  | Updated in next revision CES REPLY: Closed. |  |  | Closed.
3 | grounding of panel to be added too. 3 separate earth bar shall be considered PE, IS-IE, NIS-IE. |  |  | ISE and PE are included in panel CES REPLY: Please see comments inside document. |  |  | Closed.
4 | to be in accordance with cable sch |  |  | Updated in next revision CES REPLY: Closed. |  |  | Closed.
5 | this page to be moved after page |  |  | Updated in next revision CES REPLY: Closed. |  |  | Closed.
6 | comments on PLC / JBof C-1002 are applicable for C-7080 |  |  | Updated in next revision CES REPLY: Closed. |  |  | Closed.
comments revision 01 below
1 | Modify the MC logo |  |  | Format is the same as the P&ID |  |  | Closed.
2 | EL02: 1- The rear of the door shall be shown with mounted devices and wiring channel. 2-The suitable provision shall be considered for separation of 24Vdc and 230VAC in all trunking and ways. |  |  | Rear side can not be shown this is not part of the panel layout Confirmed separation of 24VDC and 230VAC in all trunking and ways |  |  | 1- Noted 2- Noted
3 | LCP shall be equipped to Ammeter as per TCL |  |  | LCP do not have a Ammeter only on the Distribution panel there is a Ammeter check P&ID |  |  | Noted
4 | EL-03: The terminal Strip code is specified, but terminal numbers shall be add too. |  |  | Updated in next revision |  |  | Noted
5 | EL01: The technical specifications shall be completed in nameplate. The below items shall be added in name plate: -The degree of protection panel -The permissible withstanding short circuit current -The total weight of panel -The insulation voltage of panel -Manufacturer date -The panel tag |  |  | Confirmed |  |  | Vendor confirmed that but any actions have not been done on document.
Rev 03
6 | PE is protective earth for panel earthing, for IS and NIS signals separate earth bar shall be considered. |  |  | Updated in next revision
7 | As per instrument cable list M25 cable gland shall be considered |  |  | Updated in next revision
8 | Required data as per attached file (in previous rev.) was not implemented.(such as name plate, special label and etc.) |  |  | Updated in next revision
9 | According to selecting Eex'd' type solenoid valve, so selected JB shall be Eex'd' too. JB protection shall be considered Eex'd' and its color shall be RAL9006 |  |  | Updated in next revision
10 | According to selecting Eex'd' type solenoid valve, so selected JB shall be Eex'd' too. JB protection shall be considered Eex'd' and its color shall be RAL9006 |  |  | As agreed the junction box remains ex'e , the color of the junction box will be updated in the next revision
11 | Required data as per attached file (in previous rev.) was not implemented.(such as name plate, special label and etc.) |  |  | Already included
12 | This is tag plate that you specified, in addition tag plate, name plate and special label (same as attached file in previous rev.) shall be specified in this document. |  |  | Already included
13 | Regarding to considering one JB for analogue input/outputs so one terminal strip and one multi cable 10Px0,75 mm² will be considered for this JB, accordingly X2 and X3 shall be merged in to one terminal strip. |  |  | Updated in next revision
14 | To be deleted |  |  | Updated in next revision
15 | This is tag plate that you specified, in addition tag plate, name plate and special label (same as attached file in previous rev.) shall be specified in this document. |  |  | Already included
16 | LCP shall be Eex'd' type JB, regarding to NIS signals contain it. accordingly its color shall be RAL9006 |  |  | As agreed the junction box remains ex'e , the color of the junction box will be updated in the next revision
17 | This is tag plate that you specified, in addition tag plate, name plate and special label (same as attached file in previous rev.) shall be specified in this document. |  |  | Already included
18 | M25 |  |  | Updated in next revision
19 | EL: Repeated Comment: The technical specifications shall be completed in nameplate. The below items shall be added in name plate: -The degree of protection panel -The permissible withstanding short circuit current -The total weight of panel -The insulation voltage of panel -Manufacturer date -The panel tag |  |  | The data that will be fixed at a later stage, there is a note made on the drawing with the data that will be incorporated into the nameplate as soon as it is known. (note6)dated in next revision