## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 16/Jun/2022 | Rev.:02
|  | Comment Sheet Ref.No.: | Doc Description: Calculation & Datasheet of Safety valves for Emergency instrument air compressor
|  | Transmittal No.: APCES-V-00150 | Doc. No.: BU-20-VD-303-IN-DSH-0068
|  | Transmittal Date: 16/06/2022 | Doc Rev.: 02
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply
1 | 1. The line does not have number in PID. Besides, please clarify why class of the line is 539D. |  |  | Class is 500C, line nr.N/A will be updated in next revision.
2 | 2. Please clarify why design pressure of PSV is less than its set pressure. |  |  | Updated in next revision
3 | 3. 52 oC |  |  | Updated in next revision
4 | Size has discrepancy with PID please modify. |  |  | Updated in next revision P&ID
5 | 4. 500C(N) |  |  | Will not be incorporated is as per P&ID
6 | As per project spec. : All safety relief valves, shall have flanged inlet and outlet connections of 300 # RF and 150 # RF respectively |  |  | Will not be incorporated as per seperate discussion by E-mail.
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21