## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 22/Jun/2022 | Rev.:02
|  | Comment Sheet Ref.No.: | Doc Description: Calculation & Datasheet of Safety valves for Nitrogen Gas Booster
|  | Transmittal No.: APCES-V-00152 | Doc. No.: BU-20-VD-303-IN-DSH-0015
|  | Transmittal Date: 22/Jun/2022 | Doc Rev.: 02
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply
1 | 2. 52 |  |  | Updated in next revision
2 | 18 Bar(a) as per PID |  |  | Updated in next revision
3 | 1.Discripancy with PID; In PID 18 bara. Please clarify why the set pressure of the PSV is higher that the design pressure of the 1st stage compressor. |  |  | Updated in next revision P&ID
4 | Size has discrepancy with PID please modify. |  |  | Updated in next revision P&ID
5 | 26 Bar(a) as per PID |  |  | Updated in next revision
6 | 3.Discripancy with PID; In PID 26 bara. Please clarify why the set pressure of the PSV is higher that the design pressure of the 2nd compressor. |  |  | Updated in next revision P&ID
7 | As per project spec. : All safety relief valves, shall have flanged inlet and outlet connections of 300 # RF and 150 # RF respectively |  |  | Will not be incorporated as per seperate discussion by E-mail.
8 | 4. 500C(N) |  |  | Will not be incorporated is as per P&ID
9 | - Orifice designation F is not suitable for this condition and orifice G shall be used. - Sizing has some discrepancy it shall be modified.I17 |  |  | Orifice designation and sizing as per revised calculation.
10 | First page and second page of calculation have some discrepancy, sizing calculation and data sheet shall be modified. |  |  | Updated in next revision.
11 | to be reviewed |  |  | Updated in next revision, vraag naar MRC
12
13
14
15
16
17
18
19
20
21